24023-02-50-001 – HPP Rognsfossen alarm and parameter list

Document: 24023-02-50-001 – HPP Rognsfossen alarm and parameter list author: Ivan Vučina Geppert Electric d.o.o. Hrv. Mornarice 1D ¦ 21000 Split ¦ Hrvatska customer: Mr. Yngve Tranøy Voss Energi Produksjon AS, Org.nr 984 665 776 Brynalii 66, 5705 Voss, Norway

| DOCUMENT HISTORY |  |  |  |
| --- | --- | --- | --- |
| Date | Revision | Page changes | Change Reasons |

| Attachments |  |  |  |
| --- | --- | --- | --- |
| Document name | Date | Page number | Revision number |

| Document type |  |  |  |
| --- | --- | --- | --- |
| Type: | Alarm and parameter list | Date | 13.3.2025. |

Table of contents:

1	Unit 1 alarm list and fault matrix	3

2	Unit 2 alarm list and fault matrix	17

3	Common alarm list and fault matrix	23

4	Intake alarm list and fault matrix	30

5	Unit 1 parameter list	32

6	Unit 2 parameter list	40

7	Common parameter list	45

8	Intake parameter list	49

Table 1. Table of Unit 1 alarms with IDs, descriptions, and classes.	3

Table 2. Table of Unit 2 alarms with IDs, descriptions, and classes.	17

Table 3. Table of Common alarms with IDs, descriptions, and classes.	23

Table 4. Table of Intake alarms with IDs, descriptions, and classes.	30

Table 5. Table of Unit 1 parameters with IDs, descriptions, initial values, and units.	32

Table 6. Table of Unit 2 parameters with IDs, descriptions, initial values, and units.	40

Table 7.Table of Common parameters with IDs, descriptions, initial values, and units.	45

Table 8. Table of Intake parameters with IDs, descriptions, initial values, and units.	49

Unit 1 alarm list and fault matrix

Table 1. Table of Unit 1 alarms with IDs, descriptions, and classes.

| Alarm no. | Alarm system | Alarm name | Alarm description | Alarm type |
| --- | --- | --- | --- | --- |
| 17 | Unit 1 Turbine +1MEA01 | Wicket gate position - sensor error | Alarm is triggered when the current signal exceeds the nominal limits, which are 4mA and 20mA. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Quick shutdown |
| 18 | Unit 1 Turbine +1MEA01 | Wicket gate position - positioning error | Alarm is triggered when the absolute difference between the measured position and the reference value is higher than the limit. | Quick shutdown |
| 19 | Unit 1 Turbine +1MEA01 | Runner position - sensor error | Alarm is triggered when the current signal exceeds the nominal limits, which are 4mA and 20mA. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Quick shutdown |
| 20 | Unit 1 Turbine +1MEA01 | Runner position - positioning error | Alarm is triggered when the absolute difference between the measured position and the reference value is higher than the limit. | Quick shutdown |
| 24 | Unit 1 Turbine +1MEA01 | Turbine bearing temperature measurement - error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 28 | Unit 1 Turbine +1MEA01 | Turbine not closed | Alarm is triggered if the turbine is not closed, while the Unit is in the state that dictates that the turbine should be closed. | Alarm |
| 29 | Unit 1 Turbine +1MEA01 | Turbine bearing temperature high (-111) | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Alarm |
| 30 | Unit 1 Turbine +1MEA01 | Wicket gate disturbance monitor triggered | Alarm is triggered if the wicket gate disturbance sensor declares that one or more wicket gates have disturbed position. | Quick shutdown |
| 31 | Unit 1 Turbine +1MEA01 | Turbine bearing temperature too high (-111) | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 96 | Unit 1 Waterway | Main inlet valve - signalization error | Alarm is triggered when both limit switches are activated or deactivated simultaneously. | Quick shutdown |
| 97 | Unit 1 Waterway | Main inlet valve - opening time too long | Alarm is triggered when the valve open command is activated, and the valve fails to open within the time specified in the system parameters | Quick shutdown |
| 98 | Unit 1 Waterway | Main inlet valve - closing time too long | Alarm is triggered when the valve close command is activated, and the valve fails to close within the time specified in the system parameters | Quick shutdown |
| 99 | Unit 1 Waterway | Main inlet valve - self-closure | Alarm is triggered when the valve, which is initially in the open state, begins to close, despite the absence of a command to close. | Quick shutdown |
| 114 | Unit 1 Waterway | Penstock pressure measurement (-101A) - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters, or digital signal is indicating that the measured value has very low value. | Quick shutdown |
| 117 | Unit 1 Waterway | Turbine pressure measurement (-102A) - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters, or digital signal is indicating that the measured value has very low value. | Quick shutdown |
| 122 | Unit 1 Waterway | MIV pump CB (-F51) - OFF | Alarm is triggered when CB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Quick shutdown |
| 123 | Unit 1 Waterway | MIV pump oil heater MCB (-F59) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Quick shutdown |
| 124 | Unit 1 Waterway | MIV pump contactor (-K51) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Quick shutdown |
| 125 | Unit 1 Waterway | MIV pump oil pressure (-32B) - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters, or digital signal is indicating that the measured value has very low value. | Quick shutdown |
| 126 | Unit 1 Waterway | MIV pump oil level (-398A) - low | Alarm is triggered when the measurement surpasses the low-value threshold set in the system parameters, or digital signal is indicating that the measured value has low value. | Start interlock |
| 127 | Unit 1 Waterway | MIV pump oil level (-398B) - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters, or digital signal is indicating that the measured value has very low value. | Quick shutdown |
| 128 | Unit 1 Generator +1MKA10 | U winding temperature measurement - sensor error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 129 | Unit 1 Generator +1MKA10 | U winding temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 130 | Unit 1 Generator +1MKA10 | U winding temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 131 | Unit 1 Generator +1MKA10 | V winding temperature measurement - sensor error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 132 | Unit 1 Generator +1MKA10 | V winding temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 133 | Unit 1 Generator +1MKA10 | V winding temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 134 | Unit 1 Generator +1MKA10 | W winding temperature measurement - sensor error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 135 | Unit 1 Generator +1MKA10 | W winding temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 136 | Unit 1 Generator +1MKA10 | W winding temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 160 | Unit 1 Generator +1MKA10 | D bearing temperature measurement - sensor error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 161 | Unit 1 Generator +1MKA10 | D bearing temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 162 | Unit 1 Generator +1MKA10 | D bearing temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 172 | Unit 1 Generator +1MKA10 | N bearing temperature measurement - sensor error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 173 | Unit 1 Generator +1MKA10 | N bearing temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 174 | Unit 1 Generator +1MKA10 | N bearing temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 175 | Unit 1 Generator +1MKA10 | T bearing temperature measurement sensor error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 176 | Unit 1 Generator +1MKA10 | T bearing temperature measurement high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 177 | Unit 1 Generator +1MKA10 | T bearing temperature measurement too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 178 | Unit 1 Generator +1MKA10 | Air outlet temperature sensor error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Alarm |
| 179 | Unit 1 Generator +1MKA10 | Air outlet temperature high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 180 | Unit 1 Generator +1MKA10 | Air outlet temperature too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 189 | Unit 1 Generator +1MKA10 | N bearing oil level (-F2-2) - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Normal shutdown |
| 190 | Unit 1 Generator +1MKA10 | N bearing oil level (-F2-1) - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters, or digital signal is indicating that the measured value has very low value. | Quick shutdown |
| 191 | Unit 1 Generator +1MKA10 | D bearing oil level (-F3-1) - too low | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 208 | Unit 1 Generator +1MKA10 | DE bearing working hours - warning | Alarm is triggered when the bearing lubrication operating hours surpass the alarm value set in the system parameters. | Start interlock |
| 209 | Unit 1 Generator +1MKA10 | DE bearing working hours - trip | Alarm is triggered when the bearing lubrication operating hours surpass the trip value set in the system parameters. | Normal shutdown |
| 212 | Unit 1 Generator +1MKA10 | NDE bearing working hours - warning | Alarm is triggered when the bearing lubrication operating hours surpass the alarm value set in the system parameters. | Start interlock |
| 213 | Unit 1 Generator +1MKA10 | NDE bearing working hours - trip | Alarm is triggered when the bearing lubrication operating hours surpass the trip value set in the system parameters. | Normal shutdown |
| 216 | Unit 1 Generator +1MKA10 | Main speed measurement - error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point or damage to the sensor. | Alarm |
| 217 | Unit 1 Generator +1MKA10 | Redundant speed measurement - error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point or damage to the sensor. | Normal shutdown |
| 219 | Unit 1 control and prot. +1CJA01 | Main speed meas. and frequency meas. difference too high | Alarm is triggered when the difference between the speed measurement and the frequency measurement exceeds the limit set in the system parameters. | Alarm |
| 220 | Unit 1 control and prot. +1CJA01 | Generator overspeed alarm (-K311) | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Alarm |
| 221 | Unit 1 control and prot. +1CJA01 | Generator overspeed trip (-K312) | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Emergency shutdown |
| 222 | Unit 1 Generator +1MKA10 | Generator pendulum overspeed trip | Alarm is triggered when the pendulum system detects that the generator is rotating in dangerouslsy high speed. | Emergency shutdown |
| 224 | Unit 1 control and prot. +1CJA01 | Generator heater CB (-F57) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 225 | Unit 1 control and prot. +1CJA01 | Generator heater contactor (-K57) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 236 | Unit 1 Generator +1MKA10 | Generator voltage transformator MCB (-F5) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 240 | Unit 1 Generator +1MKA10 | Oil relief system all pumps error (-F52, -K52, -F53, -K53) | Alarm is triggered when all pumps in Oil relief system fail. | Normal shutdown |
| 241 | Unit 1 Generator +1MKA10 | Oil relief pump 1 MCB (-F52) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 242 | Unit 1 Generator +1MKA10 | Oil relief pump 1 contactor (-K52) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 243 | Unit 1 Generator +1MKA10 | Oil relief pump 2 MCB (-F53) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 244 | Unit 1 Generator +1MKA10 | Oil relief pump 2 contactor (-K53) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 245 | Unit 1 Generator +1MKA10 | Oil relief system oil level (-9.1) - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters, or digital signal is indicating that the measured value has very low value. | Quick shutdown |
| 247 | Unit 1 Generator +1MKA10 | Oil relief system oil level signalization (-F9.1) - error | Alarm is triggered when both the 'ON' and 'OFF' indications are either both inactive or both active. | Alarm |
| 248 | Unit 1 Generator +1MKA10 | T bearing oil temperature measurement - error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 249 | Unit 1 Generator +1MKA10 | T bearing oil temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 250 | Unit 1 Generator +1MKA10 | T bearing oil temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 251 | Unit 1 Generator +1MKA10 | N bearing oil temperature measurement - error | Alarm is triggered when the sensor signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 252 | Unit 1 Generator +1MKA10 | N bearing oil temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 253 | Unit 1 Generator +1MKA10 | N bearing oil temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 254 | Unit 1 Generator +1MKA10 | Oil relief pump 1 unable to build up pressure | The alarm is triggered if the pump fails to build sufficient pressure to ensure the proper functioning of the system. | Alarm |
| 255 | Unit 1 Generator +1MKA10 | Oil relief pump 2 unable to build up pressure | The alarm is triggered if the pump fails to build sufficient pressure to ensure the proper functioning of the system. | Alarm |
| 268 | Unit 1 transformer +1BAT10 | Oil temperature sensor error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point or damage to the sensor. | Normal shutdown |
| 269 | Unit 1 transformer +1BAT10 | Oil temperature (-S1//+K3) - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 270 | Unit 1 transformer +1BAT10 | Oil temperature (-S2//+K3) - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 274 | Unit 1 transformer +1BAT10 | Gas alarm (-S1//+K1) | Alarm is triggerd when transformer gas indicator is indicating an alarm state. | Start interlock |
| 280 | Unit 1 transformer +1BAT10 | Pressure trip (-S1//+K4) | Alarm is triggerd when transformer pressure indicator is indicating a trip state. | Quick shutdown |
| 281 | Unit 1 transformer +1BAT10 | Control MCB (-F56) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 282 | Unit 1 transformer +1BAT10 | Oil pump not running | Alarm is triggered when system detects if transformator oil pump is not runing when the conditions for running are fulfilled. | Normal shutdown |
| 283 | Unit 1 transformer +1BAT10 | Gas trip (-S2//+K1) | Alarm is triggerd when transformer gas indicator is indicating a trip state. | Quick shutdown |
| 284 | Unit 1 transformer +1BAT10 | Oil level (-S2//+K2) - low | Alarm is triggerd when transformer oil level indicator is indicating a trip state. | Quick shutdown |
| 285 | Unit 1 transformer +1BAT10 | Oil level (-S1//+K2) - high | Alarm is triggerd when transformer oil level indicator is indicating a trip state. | Start interlock |
| 286 | Unit 1 transformer +1BAT10 | Water flow monitor (-S1//+K5) - not OK | Alarm is triggerd when transformer water flow indicator is indicating a trip state. | Quick shutdown |
| 287 | Unit 1 transformer +1BAT10 | Water pressure (-S1//+K6) - too low | Alarm is triggerd when transformer water pressure indicator is indicating a trip state. | Quick shutdown |
| 322 | Unit 1 control and prot. +1CJA01 | Excitation contactor (-Q13, -Q13A) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Emergency shutdown |
| 323 | Unit 1 Exc. device (-DECS-250) | Watchdog fault | Alarm is triggered when the live contact of the protection device is not active, indicating a potential fault status. | Emergency shutdown |
| 324 | Unit 1 Exc. device (-DECS-250) | Voltage not built | Alarm is triggered when the START/STOP command is activated for the excitation device, and it fails to perform the requested operation within the time limit specified in the system parameters. | Normal shutdown |
| 327 | Unit 1 Exc. device (-DECS-250) | Alarm from device | Alarm is triggered when excitation device alarm is active. | Alarm |
| 328 | Unit 1 Exc. device (-DECS-250) | Limiter active | Alarm is triggered when excitation device limiter is active. | Alarm |
| 336 | Unit 1 Exc. device (-DECS-250) | Trip from device | Alarm is triggered when excitation device trip is active. | Emergency shutdown |
| 352 | Unit 1 gen. prot. (-7UM85) | Device fault | Alarm is triggered when the live contact of the protection device is not active, indicating a potential fault status. | Emergency shutdown |
| 354 | Unit 1 gen. prot. (-7UM85) | Trip from device | Alarm is triggered when protection device trip 1 is active. | Emergency shutdown |
| 363 | Unit 1 trafo. prot. (-7SX800) | Device fault | Alarm is triggered when the live contact of the protection device is not active, indicating a potential fault status. | Emergency shutdown |
| 365 | Unit 1 trafo. prot. (-7SX800) | Trip from device | Alarm is triggered when protection device trip 1 is active. | Emergency shutdown |
| 368 | Unit 1 Control - Auto mode | Speed measurement error | Alarm is triggered when all speed measuremens are in a state of fault, or when difference between multiple speed measuremens is too high. | Alarm |
| 370 | Unit 1 Control - Auto mode | Minimal distributor openness | Alarm is triggered when turbine openness is below certain threshold. It prevents generator from working in motor mode. | Alarm |
| 371 | Unit 1 Control - Auto mode | Turbine pressure is not in allowed limits | Alarm is triggered when turbine pressure is below certain threshold. It triggers auto restart function of the Unit. | Alarm |
| 374 | Unit 1 Control - Auto mode | Can not start automatically | Alarm is triggered when auto restart function is started, but could not start the Unit. | Alarm |
| 384 | Unit 1 Control - Auto mode | Emergency shutdown button pressed (-S301) | Alarm is triggered when emergency shutdown pushbutton is pressed. | Emergency shutdown |
| 385 | Unit 1 Control - Auto mode | Emergency shutdown relay tripped (-K301) | Alarm is triggered when emergency shutdown is active. | Alarm |
| 386 | Transformer feeder 1 +AKA01 | Generator circuit breaker - signalization error | Alarm is triggered when both the 'open' and 'closed' indications are either both inactive or both active. | Emergency shutdown |
| 387 | Transformer feeder 1 +AKA01 | Generator circuit breaker - opening coil failure | Alarm is triggered when the GCB fails to open despite receiving the open command. | Emergency shutdown |
| 388 | Transformer feeder 1 +AKA01 | Generator circuit breaker - self opening | Alarm is triggered when the GCB, initially in the closed state, is set to the open state without the presence of a command to open | Emergency shutdown |
| 389 | Unit 1 control and prot. +1CJA01 | Digital inputs power supply MCB (-F31) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 390 | Unit 1 control and prot. +1CJA01 | External signals power supply MCB (-F36) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 391 | Unit 1 control and prot. +1CJA01 | Analog inputs power supply MCB (-F33) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 392 | Unit 1 control and prot. +1CJA01 | Maintenance mode activated (-S100) | Alarm is triggered when when maintenance mode is active. | Emergency shutdown |
| 394 | Unit 1 control and prot. +1CJA01 | 24VDC MCBs group (-F34, -F38, -F39, -F40, -F41, -F42) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 395 | Unit 1 control and prot. +1CJA01 | Quick shutdown relay tripped (-K401) | Alarm is triggered when quick shutdown is active. | Alarm |
| 396 | Unit 1 control and prot. +1CJA01 | Digital outputs power supply MCB (-F32) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 398 | Unit 1 control and prot. +1CJA01 | ESD trip from Common +0CJA01 | Alarm is triggered when Emergency shutdown trip is sent from Common. It triggers Emergency shutdown sequence of the Unit. | Emergency shutdown |
| 399 | Unit 1 control and prot. +1CJA01 | QSD trip from Common +0CJA01 | Alarm is triggered when Quick shutdown trip is sent from Common. It triggers Quick shutdown sequence of the Unit. | Quick shutdown |
| 400 | Unit 1 control and prot. +1CJA01 | Start interlock from Common +0CJA01 | Alarm is triggered when Start interlock is sent from Common. It triggers Start interlock alarm in the Unit. | Start interlock |
| 401 | Unit 1 control and prot. +1CJA01 | NSD trip from Common +0CJA01 | Alarm is triggered when Normal shutdown trip is sent from Common. It triggers Normal shutdown sequence of the Unit. | Normal shutdown |
| 405 | Unit 1 Communication | Common communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 406 | Unit 1 Communication | Generator measurement device SENTRON comm. error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 407 | Unit 1 Communication | Generator protection device 7UM85 - communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 409 | Unit 1 Communication | Trafo. protection device 7SX800 - communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 414 | Unit 1 Communication | Excitation device communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 415 | Unit 1 control and prot. +1CJA01 | 220VDC MCBs group (-F130, -F131, -F132, -F133, -F134) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 418 | Unit 1 Control | Active power measurement fault | Alarm is triggered when there is no information available for measurement. | Emergency shutdown |
| 419 | Unit 1 Control | Speed measurement fault | Alarm is triggered when there is no information available for measurement or when the absolute difference between measurements surpasses the limit set in system parameters. In the case of a single sensor, the fault is attributed to sensor error. If there are two sensors, the fault may result from errors in both sensors or measurements exceeding the specified limit. In the case of three sensors, the fault could be due to errors in two sensors or all three measurements exceeding the limit. | Alarm |
| 420 | Unit 1 control and prot. +1CJA01 | Wicket gate heater MCB (-F58) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 432 | Unit 1 Start Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Normal shutdown |
| 433 | Unit 1 NSD Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Quick shutdown |
| 434 | Unit 1 QSD Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Emergency shutdown |
| 435 | Unit 1 ESD Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Alarm |
| 436 | Unit 1 Start Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Normal shutdown |
| 437 | Unit 1 NSD Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Quick shutdown |
| 438 | Unit 1 QSD Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Emergency shutdown |
| 439 | Unit 1 ESD Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Alarm |
| 454 | Unit 1 control and prot. +1CJA01 | Grid VT MCB (-F3, -F2) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Normal shutdown |
| 468 | Transformer feeder 1 +AKA01 | Generator circuit breaker spring not charged | Alarm is triggered when the generator circuit breaker spring is not charged within time set in the parameters. | Alarm |
| 469 | Unit 1 Generator +1MKA10 | Generator neutral voltage measurement MCB (-F1) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 511 | Unit 1 control and prot. +1CJA01 | Multimeter (SENTRON) power supply MCB (-F44) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 678 | Unit 1 Cooling water system | Flow temperature high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters, or digital signal is indicating that the measured value has high value. | Start interlock |
| 679 | Unit 1 Cooling water system | Flow temperature too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 686 | Unit 1 Cooling water system | Valve closing time too long | Alarm is triggered when the valve close command is activated, and the valve fails to close within the time specified in the system parameters | Normal shutdown |
| 687 | Unit 1 Cooling water system | Valve opening time too long | Alarm is triggered when the valve open command is activated, and the valve fails to open within the time specified in the system parameters | Normal shutdown |
| 688 | Unit 1 Cooling water system | Valve signalization error | The alarm is triggered when both the open and close signals are activated simultaneously | Alarm |
| 689 | Unit 1 Cooling water system | Filter power supply MCB (-F55) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 690 | Unit 1 Cooling water system | Valve power supply MCB (-F151) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Normal shutdown |
| 692 | Unit 1 Cooling water system | Valve open contactor (-K151) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 693 | Unit 1 Cooling water system | Valve close contactor (-K152) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 694 | Unit 1 Cooling water system | Valve ON contactor (-K1512) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 700 | Unit 1 Cooling water system | Filter clogged warning | Alarm is triggered when the duration of filter clogging exceeds the alarm time limit set in the system parameters. | Start interlock |
| 701 | Unit 1 Cooling water system | Filter clogged trip | Alarm is triggered when the duration of filter clogging exceeds the trip time limit set in the system parameters. | Quick shutdown |
| 739 | Unit 1 Drainage system | Pump 1 motor CB (-F54) - OFF | Alarm is triggered when CB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 741 | Unit 1 Drainage system | Pump 1 motor contactor (-K54) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 742 | Unit 1 Drainage system | Pump 2 motor CB (-F153) - OFF | Alarm is triggered when CB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 744 | Unit 1 Drainage system | Pump 2 motor contactor (-K153) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 745 | Unit 1 Drainage system | Turbine sealing system signalization (-146) - error | Alarm is triggered when both the 'ON' and 'OFF' indications are either both inactive or both active. | Quick shutdown |
| 746 | Unit 1 Drainage system | All pumps error (-F54, -K54, -F153, -K153) | Alarm is triggered when all pumps in Turbine drainage system fail. | Emergency shutdown |
| 754 | Unit 1 Drainage system | Turbine casing water level (-134A) - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters, or digital signal is indicating that the measured value has very high value. | Quick shutdown |
| 768 | Unit 1 Gen. prot. relay 7UM85 | Current side 1 measurement brake wire detection | Detects a break in the measurement wiring on the current side 1. | Alarm |
| 769 | Unit 1 Gen. prot. relay 7UM85 | Current side 2 measurement brake wire detection | Detects a break in the measurement wiring on the current side 2. | Alarm |
| 770 | Unit 1 Gen. prot. relay 7UM85 | Supv. ph.seq.V-Failure | Monitors incorrect phase sequence. | Alarm |
| 771 | Unit 1 Gen. prot. relay 7UM85 | Overvoltage protection -47 | Detects and protects against phase voltage imbalance or overvoltage. | Alarm |
| 772 | Unit 1 Gen. prot. relay 7UM85 | Overcurrent protection - 50/51 OC-3ph-B1 - stage 1 | Protects against against short circuits with a time delay. | Alarm |
| 773 | Unit 1 Gen. prot. relay 7UM85 | Overcurrent protection - 50/51 OC-3ph-B1 - stage 2 | Instantaneous short-circuit protection, triggered by high fault currents. | Alarm |
| 774 | Unit 1 Gen. prot. relay 7UM85 | 50/51 transformer side - stage 1 | Protects against fault overcurrent on the transformer side in the first stage. | Alarm |
| 775 | Unit 1 Gen. prot. relay 7UM85 | 50/51 transformer side - stage 2 | Protects against fault overcurrent on the transformer side in the second stage. | Alarm |
| 776 | Unit 1 Gen. prot. relay 7UM85 | Thermal overload - 49 Th.overl.-A 1 | Protects the equipment against thermal overloads. | Alarm |
| 777 | Unit 1 Gen. prot. relay 7UM85 | Undervoltage protection - 27 Undervolt.-3ph 1 - stage 1 | Detects and protects against undervoltage in the first stage. | Alarm |
| 778 | Unit 1 Gen. prot. relay 7UM85 | Undervoltage protection - 27 Undervolt.-3ph 1 - stage 2 | Detects and protects against undervoltage in the second stage. | Alarm |
| 779 | Unit 1 Gen. prot. relay 7UM85 | Overvoltage protection - 59 Overvolt.-3ph 1 - stage 1 | Detects and protects against overvoltage condition in the first stage. | Alarm |
| 780 | Unit 1 Gen. prot. relay 7UM85 | Overvoltage protection - 59 Overvolt.-3ph 1 - stage 2 | Detects and protects against overvoltage condition in the second stage. | Alarm |
| 781 | Unit 1 Gen. prot. relay 7UM85 | Underfrequency protection - 81 Underfreq.-A 1 - stage 1 | Detects and protects against system underfrequency in the first stage. | Alarm |
| 782 | Unit 1 Gen. prot. relay 7UM85 | Underfrequency protection - 81 Underfreq.-A 1 - stage 2 | Detects and protects against system underfrequency in the second stage. | Alarm |
| 783 | Unit 1 Gen. prot. relay 7UM85 | Overfrequency protection - 81 Overfreq.-A 1 - stage 1 | Detects and protects against system overfrequency in the first stage. | Alarm |
| 784 | Unit 1 Gen. prot. relay 7UM85 | Overfrequency protection - 81 Overfreq.-A 1 - stage 2 | Detects and protects against system overfrequency in the second stage. | Alarm |
| 785 | Unit 1 Gen. prot. relay 7UM85 | Reverse power protection - 32R Revers.pow. 1 | Detects reverse power flow to prevent generator motoring. | Alarm |
| 786 | Unit 1 Gen. prot. relay 7UM85 | Unbalance load protection - Thermal stage 1 | Protects against thermal effects of load imbalance in the first stage. | Alarm |
| 787 | Unit 1 Gen. prot. relay 7UM85 | Overexcitation protection - stage 1 | Detects and protects against excessive excitation levels in the first stage. | Alarm |
| 788 | Unit 1 Gen. prot. relay 7UM85 | Overexcitation protection - Thermal stage | Protects against thermal damage due to excessive excitation. | Alarm |
| 789 | Unit 1 Gen. prot. relay 7UM85 | Underexcitation protection 40 - ch1 | Detects and protects against underexcitation conditions based on characteristic 1. | Alarm |
| 790 | Unit 1 Gen. prot. relay 7UM85 | Stator ground fault protection - SGF 90% MP-3ph 1 | Protects the generator stator against ground faults covering 90% of the winding. | Alarm |
| 791 | Unit 1 Gen. prot. relay 7UM85 | Breaker failure protection - 50BF Ad.CBF 1 | Detects circuit breaker failure. | Alarm |
| 792 | Unit 1 Gen. prot. relay 7UM85 | 87T Differential prot. stage 1 | Detects internal faults in generator and transformer using differential protection in the first stage. | Alarm |
| 793 | Unit 1 Gen. prot. relay 7UM85 | 87T Differential prot. stage 2 | Detects internal faults in generator and transformer using differential protection in the second stage. | Alarm |
| 794 | Unit 1 Gen. prot. relay 7UM85 | 51GN SCP 1PH 1 | Detects shaft currents via special shaft-current transformer. | Alarm |
| 795 | Unit 1 Gen. prot. relay 7UM85 | Underexcitation protection 40 - ch3 | Detects and protects against underexcitation conditions based on characteristic 3. | Alarm |
| 796 | Unit 1 Gen. prot. relay 7UM85 | spare | Alarm is triggered when the device sends an alarm state via communication. | Alarm |
| 797 | Unit 1 Gen. prot. relay 7UM85 | spare | Alarm is triggered when the device sends an alarm state via communication. | Alarm |
| 798 | Unit 1 Gen. prot. relay 7UM85 | spare | Alarm is triggered when the device sends an alarm state via communication. | Alarm |
| 799 | Unit 1 Gen. prot. relay 7UM85 | spare | Alarm is triggered when the device sends an alarm state via communication. | Alarm |
| 800 | Unit 1 Trafo. prot. relay 7SX800 | Current measurement brake wire detection | Detects interruptions or faults in the current measurement wiring. | Alarm |
| 801 | Unit 1 Trafo. prot. relay 7SX800 | Supv. ph.seq.V-Failure | Monitors the phase sequence and detects incorrect phase rotation. | Alarm |
| 802 | Unit 1 Trafo. prot. relay 7SX800 | Overcurrent protection - 50/51 OC-3ph-B1 - stage 1 | Protects against against short circuits with a time delay. | Alarm |
| 803 | Unit 1 Trafo. prot. relay 7SX800 | Overcurrent protection - 50/51 OC-3ph-B1 - stage 2 | Instantaneous short-circuit protection, triggered by high fault currents. | Alarm |
| 804 | Unit 1 Trafo. prot. relay 7SX800 | Overvolt.-47-V2 1 | Detects and protects against phase voltage imbalance or overvoltage. | Alarm |
| 805 | Unit 1 Trafo. prot. relay 7SX800 | Ground overcurrent protection - 50/51 OC-3ph-B1 - stage 1 | Protects against ground faults with a time delay, activated by lower fault currents. | Alarm |
| 806 | Unit 1 Trafo. prot. relay 7SX800 | Ground overcurrent protection - 50/51 OC-3ph-B1 - stage 2 | Instantaneous protection against ground faults triggered by high fault currents. | Alarm |
| 807 | Unit 1 Trafo. prot. relay 7SX800 | 81R Rate of f chg. 1 | Detects rapid frequency changes and provides protection against sudden grid disturbances. | Alarm |
| 808 | Unit 1 Trafo. prot. relay 7SX800 | Overvoltage protection - 59 Overvolt.-3ph 1 - stage 1 | Detects and protects against an overvoltage condition in one or more phases in the first stage. | Alarm |
| 809 | Unit 1 Trafo. prot. relay 7SX800 | Overvoltage protection - 59 Overvolt.-3ph 1 - stage 2 | Detects and protects against an overvoltage condition in one or more phases in the second stage. | Alarm |
| 810 | Unit 1 Trafo. prot. relay 7SX800 | Undervoltage protection - 27 Undervolt.-3ph 1 - stage 1 | Detects and protects against a drop in voltage in one or more phases in the first stage. | Alarm |
| 811 | Unit 1 Trafo. prot. relay 7SX800 | Undervoltage protection - 27 Undervolt.-3ph 1 - stage 2 | Detects and protects against a drop in voltage in one or more phases in the second stage. | Alarm |
| 812 | Unit 1 Trafo. prot. relay 7SX800 | Overfrequency protection - 81 Overfreq.-A 1 - stage 1 | Detects and protects against an increase in system frequency in the first stage. | Alarm |
| 813 | Unit 1 Trafo. prot. relay 7SX800 | Overfrequency protection - 81 Overfreq.-A 1 - stage 2 | Detects and protects against an increase in system frequency in the second stage. | Alarm |
| 814 | Unit 1 Trafo. prot. relay 7SX800 | Underfrequency protection - 81 Underfreq.-A 1 - stage 1 | Detects and protects against a decrease in system frequency in the first stage. | Alarm |
| 815 | Unit 1 Trafo. prot. relay 7SX800 | Underfrequency protection - 81 Underfreq.-A 1 - stage 2 | Detects and protects against a decrease in system frequency in the second stage. | Alarm |
| 816 | Unit 1 Trafo. prot. relay 7SX800 | 59 Overvolt.-V0 1 | Detects and protects against zero-sequence overvoltage, indicating potential ground faults or unbalanced system conditions. | Alarm |
| 817 | Unit 1 Trafo. prot. relay 7SX800 | Thermal overload - 49 Th.overl.-A 1 | Protects the equipment against thermal overloads. | Alarm |

Unit 2 alarm list and fault matrix

Table 2. Table of Unit 2 alarms with IDs, descriptions, and classes.

| Alarm no. | Alarm system | Alarm name | Alarm description | Alarm type |
| --- | --- | --- | --- | --- |
| 15 | Unit 2 Turbine +2MEA01 | Distributor position - sensor error | Alarm is triggered when the absolute difference between the measured position and the reference value is higher than the limit. | Quick shutdown |
| 16 | Unit 2 Turbine +2MEA01 | Distributor position - positioning error | Alarm is triggered when the current signal exceeds the nominal limits, which are 4mA and 20mA. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Quick shutdown |
| 28 | Unit 2 Turbine +2MEA01 | Turbine not closed | Alarm is triggered due to spring ling monitoring fault. | Alarm |
| 29 | Unit 2 Turbine +2MEA01 | ESD valve signalization error | Alarm is triggered when both limit switches are activated simultaneously. | Quick shutdown |
| 31 | Unit 2 Turbine +2MEA01 | Wicket gate heater MCB (-F54) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 96 | Unit 2 Waterway | Main inlet valve - signalization error | Alarm is triggered when both limit switches are activated simultaneously. | Quick shutdown |
| 97 | Unit 2 Waterway | Main inlet valve - opening time too long | Alarm is triggered when the valve open command is activated, and the valve fails to open within the time specified in the system parameters | Quick shutdown |
| 98 | Unit 2 Waterway | Main inlet valve - closing time too long | Alarm is triggered when the valve close command is activated, and the valve fails to close within the time specified in the system parameters | Quick shutdown |
| 99 | Unit 2 Waterway | Main inlet valve - self-closure | Alarm is triggered when the valve, which is initially in the open state, begins to close, despite the absence of a command to close. | Quick shutdown |
| 123 | Unit 2 Waterway | MIV heater MCB (-F55) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 128 | Unit 2 Generator +2MKA10 | U winding temperature measurement - sensor errror | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 129 | Unit 2 Generator +2MKA10 | U winding temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 130 | Unit 2 Generator +2MKA10 | U winding temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 131 | Unit 2 Generator +2MKA10 | V winding temperature measurement - sensor errror | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 132 | Unit 2 Generator +2MKA10 | V winding temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 133 | Unit 2 Generator +2MKA10 | V winding temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 134 | Unit 2 Generator +2MKA10 | W winding temperature measurement - sensor errror | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 135 | Unit 2 Generator +2MKA10 | W winding temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 136 | Unit 2 Generator +2MKA10 | W winding temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 160 | Unit 2 Generator +2MKA10 | D bearing temperature measurement - sensor error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 161 | Unit 2 Generator +2MKA10 | D bearing temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 162 | Unit 2 Generator +2MKA10 | D bearing temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 172 | Unit 2 Generator +2MKA10 | N bearing temperature measurement - sensor error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 173 | Unit 2 Generator +2MKA10 | N bearing temperature measurement - high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 174 | Unit 2 Generator +2MKA10 | N bearing temperature measurement - too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 175 | Unit 2 Generator +2MKA10 | T bearing temperature sensor error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Normal shutdown |
| 176 | Unit 2 Generator +2MKA10 | T bearing 6 temperature high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 177 | Unit 2 Generator +2MKA10 | T bearing 6 temperature too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 179 | Unit 2 Generator +2MKA10 | Air outlet temperature high | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Start interlock |
| 180 | Unit 2 Generator +2MKA10 | Air outlet temperature too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 208 | Unit 2 Generator +2MKA10 | DE bearing working hours - warning | Alarm is triggered when the bearing lubrication operating hours surpass the alarm value set in the system parameters. | Start interlock |
| 209 | Unit 2 Generator +2MKA10 | DE bearing working hours - trip | Alarm is triggered when the bearing lubrication operating hours surpass the trip value set in the system parameters. | Normal shutdown |
| 212 | Unit 2 Generator +2MKA10 | NDE bearing working hours - warning | Alarm is triggered when the bearing lubrication operating hours surpass the alarm value set in the system parameters. | Start interlock |
| 213 | Unit 2 Generator +2MKA10 | NDE bearing working hours - trip | Alarm is triggered when the bearing lubrication operating hours surpass the trip value set in the system parameters. | Normal shutdown |
| 219 | Unit 2 control and prot. +2CJA01 | Main speed meas. and frequency meas. difference too high | Alarm is triggered when the difference between the speed measurement and the frequency measurement exceeds the limit set in the system parameters. | Alarm |
| 220 | Unit 2 control and prot. +2CJA01 | Overspeed alarm | Alarm is triggered when the measurement surpasses the high-value threshold set in the system parameters. | Alarm |
| 221 | Unit 2 control and prot. +2CJA01 | Generator overspeed trip (-K311) | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Emergency shutdown |
| 224 | Unit 2 control and prot. +2CJA01 | Generator heater CB (-F53) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 225 | Unit 2 control and prot. +2CJA01 | Generator heater contactor (-K53) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 241 | Unit 2 Generator +2MKA10 | Oil flow monitor not OK | Alarm is triggered when oil flow system declares fault state. | Quick shutdown |
| 352 | Unit 2 Gen. prot. relay (-7UM85) | Device fault | Alarm is triggered when the live contact of the protection device is not active, indicating a potential fault status. | Emergency shutdown |
| 354 | Unit 2 Gen. prot. relay (-7UM85) | Trip from device | Alarm is triggered when protection device trip 1 is active. | Emergency shutdown |
| 368 | Unit 2 Control - Auto mode | Speed measurement error | Alarm is triggered when all speed measuremens are in a state of fault, or when difference between multiple speed measuremens is too high. | Alarm |
| 370 | Unit 2 Control - Auto mode | Minimal distributor openness | Alarm is triggered when turbine openness is below certain threshold. It prevents generator from working in motor mode. | Alarm |
| 371 | Unit 2 Control - Auto mode | Turbine pressure is not in allowed limits | Alarm is triggered when turbine pressure is below certain threshold. It triggers auto restart function of the Unit. | Alarm |
| 374 | Unit 2 Control - Auto mode | Can not start automatically | Alarm is triggered when auto restart function is started, but could not start the Unit. | Alarm |
| 384 | Unit 2 control and prot. +2CJA01 | Emergency shutdown button pressed (-S301) | Alarm is triggered when emergency shutdown pushbutton is pressed. | Emergency shutdown |
| 385 | Unit 2 control and prot. +2CJA01 | Emergency shutdown relay tripped (-K301) | Alarm is triggered when emergency shutdown is active. | Alarm |
| 386 | Unit 2 Generator +2MKA10 | Generator circuit breaker - signalization error | Alarm is triggered when both the 'open' and 'closed' indications are either both inactive or both active. | Emergency shutdown |
| 387 | Unit 2 Generator +2MKA10 | Generator circuit breaker - opening coil failure | Alarm is triggered when the GCB fails to open despite receiving the open command. | Emergency shutdown |
| 388 | Unit 2 Generator +2MKA10 | Generator circuit breaker - self opening | Alarm is triggered when the GCB, initially in the closed state, is set to the open state without the presence of a command to open | Emergency shutdown |
| 389 | Unit 2 control and prot. +2CJA01 | Digital inputs power supply MCB (-F31) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 390 | Unit 2 control and prot. +2CJA01 | External signals power supply MCB (-F36) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 391 | Unit 2 control and prot. +2CJA01 | Analog inputs power supply MCB (-F33) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 392 | Unit 2 control and prot. +2CJA01 | Maintenance mode activated (-S100) | Alarm is triggered when when maintenance mode is active. | Emergency shutdown |
| 394 | Unit 2 control and prot. +2CJA01 | 24VDC MCBs group (-F34, -F38, -F39) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 395 | Unit 2 control and prot. +2CJA01 | Quick shutdown relay tripped (-K401) | Alarm is triggered when quick shutdown is active. | Alarm |
| 396 | Unit 2 control and prot. +2CJA01 | Digital outputs power supply (-F32) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 398 | Unit 2 control and prot. +2CJA01 | ESD trip from Common +0CJA01 | Alarm is triggered when Emergency shutdown trip is sent from Common. It triggers Emergency shutdown sequence of the Unit. | Emergency shutdown |
| 399 | Unit 2 control and prot. +2CJA01 | QSD trip from Common +0CJA01 | Alarm is triggered when Quick shutdown trip is sent from Common. It triggers Quick shutdown sequence of the Unit. | Quick shutdown |
| 400 | Unit 2 control and prot. +2CJA01 | Start interlock from Common +0CJA01 | Alarm is triggered when Start interlock is sent from Common. It triggers Start interlock alarm in the Unit. | Start interlock |
| 401 | Unit 2 control and prot. +2CJA01 | NSD trip from Common +0CJA01 | Alarm is triggered when Normal shutdown trip is sent from Common. It triggers Normal shutdown sequence of the Unit. | Normal shutdown |
| 405 | Unit 2 Communication | Common communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 407 | Unit 2 Communication | Generator protection device 7UM85 - communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 411 | Unit 2 Communication | BFA cubicle communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Emergency shutdown |
| 418 | Unit 2 Control | Active power measurement fault | Alarm is triggered when there is no information available for measurement. | Emergency shutdown |
| 419 | Unit 2 Control | Speed measurement fault | Alarm is triggered when there is no information available for measurement or when the absolute difference between measurements surpasses the limit set in system parameters. In the case of a single sensor, the fault is attributed to sensor error. If there are two sensors, the fault may result from errors in both sensors or measurements exceeding the specified limit. In the case of three sensors, the fault could be due to errors in two sensors or all three measurements exceeding the limit. | Alarm |
| 432 | Unit 2 Start Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Normal shutdown |
| 433 | Unit 2 NSD Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Quick shutdown |
| 434 | Unit 2 QSD Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Emergency shutdown |
| 435 | Unit 2 ESD Sequence | Sequence too long | Alarm is triggered when the sequence duration surpasses the duration set in the system parameters. | Alarm |
| 436 | Unit 2 Start Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Normal shutdown |
| 437 | Unit 2 NSD Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Quick shutdown |
| 438 | Unit 2 QSD Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Emergency shutdown |
| 439 | Unit 2 ESD Sequence | Step too long | Alarm is triggered when the sequence step duration surpasses the duration set in the sequence parameters. | Alarm |
| 448 | Unit 2 Generator +2MKA10 | Generator circuit breaker tripped | Alarm is triggered when GCB is tripped. | Emergency shutdown |
| 449 | Unit 2 Generator +2MKA10 | GCB not ready to close | Alarm is triggered when GCB is not ready to close. Posible causes are spring not charged, undervoltage coil is not activated or trip is active. | Alarm |
| 451 | Unit 2 control and prot. +2CJA01 | GCB control MCB (-F132) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 454 | Unit 2 control and prot. +2CJA01 | Grid VT MCB (-F3, -F1, -F2) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 511 | Unit 2 control and prot. +2CJA01 | 220VDC MCBs group (-F130, -F131, -F132) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 768 | Unit 2 Gen. prot. relay 7UM85 | Current measurement brake wire detection | Detects interruptions or faults in the current measurement wiring. | Alarm |
| 769 | Unit 2 Gen. prot. relay 7UM85 | Supv. ph.seq.V-Failure | Monitors the phase sequence and detects incorrect phase rotation. | Alarm |
| 770 | Unit 2 Gen. prot. relay 7UM85 | Overcurrent protection - 50/51 OC-3ph-B1 - stage 1 | Protects against against short circuits with a time delay. | Alarm |
| 771 | Unit 2 Gen. prot. relay 7UM85 | Overcurrent protection - 50/51 OC-3ph-B1 - stage 2 | Instantaneous short-circuit protection, triggered by high fault currents. | Alarm |
| 772 | Unit 2 Gen. prot. relay 7UM85 | Overvolt.-47-V2 1 | Detects and protects against phase voltage imbalance or overvoltage. | Alarm |
| 773 | Unit 2 Gen. prot. relay 7UM85 | Ground overcurrent protection - 50/51 OC-3ph-B1 - stage 1 | Protects against ground faults with a time delay, activated by lower fault currents. | Alarm |
| 774 | Unit 2 Gen. prot. relay 7UM85 | Ground overcurrent protection - 50/51 OC-3ph-B1 - stage 2 | Instantaneous protection against ground faults triggered by high fault currents. | Alarm |
| 775 | Unit 2 Gen. prot. relay 7UM85 | 81R Rate of f chg. 1 | Detects rapid frequency changes and provides protection against sudden grid disturbances. | Alarm |
| 776 | Unit 2 Gen. prot. relay 7UM85 | Overvoltage protection - 59 Overvolt.-3ph 1 - stage 1 | Detects and protects against an overvoltage condition in one or more phases in the first stage. | Alarm |
| 777 | Unit 2 Gen. prot. relay 7UM85 | Overvoltage protection - 59 Overvolt.-3ph 1 - stage 2 | Detects and protects against an overvoltage condition in one or more phases in the second stage. | Alarm |
| 778 | Unit 2 Gen. prot. relay 7UM85 | Undervoltage protection - 27 Undervolt.-3ph 1 - stage 1 | Detects and protects against a drop in voltage in one or more phases in the first stage. | Alarm |
| 779 | Unit 2 Gen. prot. relay 7UM85 | Undervoltage protection - 27 Undervolt.-3ph 1 - stage 2 | Detects and protects against a drop in voltage in one or more phases in the second stage. | Alarm |
| 780 | Unit 2 Gen. prot. relay 7UM85 | Overfrequency protection - 81 Overfreq.-A 1 - stage 1 | Detects and protects against an increase in system frequency in the first stage. | Alarm |
| 781 | Unit 2 Gen. prot. relay 7UM85 | Overfrequency protection - 81 Overfreq.-A 1 - stage 2 | Detects and protects against an increase in system frequency in the second stage. | Alarm |
| 782 | Unit 2 Gen. prot. relay 7UM85 | Underfrequency protection - 81 Underfreq.-A 1 - stage 1 | Detects and protects against a decrease in system frequency in the first stage. | Alarm |
| 783 | Unit 2 Gen. prot. relay 7UM85 | Underfrequency protection - 81 Underfreq.-A 1 - stage 2 | Detects and protects against a decrease in system frequency in the second stage. | Alarm |
| 784 | Unit 2 Gen. prot. relay 7UM85 | 59 Overvolt.-V0 1 | Detects and protects against zero-sequence overvoltage, indicating potential ground faults or unbalanced system conditions. | Alarm |
| 785 | Unit 2 Gen. prot. relay 7UM85 | Thermal overload - 49 Th.overl.-A 1 | Protects the equipment against thermal overloads. | Alarm |

Common alarm list and fault matrix

Table 3. Table of Common alarms with IDs, descriptions, and classes.

| Alarm no. | Alarm system | Alarm name | Alarm description | Alarm type |
| --- | --- | --- | --- | --- |
| 25 | Unit 1 Turbine +1MEA10 | Tail water level - sensor error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Alarm |
| 32 | Auxiliary supply cubicle +0BFA01 | Hydraulic oil pump 1 contactor (-K51) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 33 | Auxiliary supply cubicle +0BFA01 | Hydraulic oil pump 1 CB (-F51) - OFF | Alarm is triggered when circuit breaker is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 38 | Auxiliary supply cubicle +0BFA01 | Hydraulic oil pump 2 contactor (-K52) - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 39 | Auxiliary supply cubicle +0BFA01 | Hydraulic oil pump 2 CB (-F52) - OFF | Alarm is triggered when circuit breaker is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 56 | Auxiliary supply cubicle +0BFA01 | All hydraulic pumps error (F51, -F52, -K51, K52) | Alarm is triggered when all pumps are in an error state. | Quick shutdown |
| 69 | HPU +1MEX10 | Accumulator pressure too low (-255F.1) | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters. | Emergency shutdown |
| 70 | HPU +1MEX10 | Accumulator pressure measurement (-) - low | Alarm is triggered when the measurement falls below the low-value threshold set in the system parameters. | Start interlock |
| 77 | HPU +1MEX10 | Oil level low (-227E) | Alarm is triggered when the measurement falls below the low-value threshold set in the system parameters. | Start interlock |
| 78 | HPU +1MEX10 | Oil level measurement too low (-227G) | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters. | Quick shutdown |
| 84 | HPU +1MEX10 | Oil temperature measurement too high (-258) | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 85 | HPU +1MEX10 | Pressure filter clogging warning (-227H) | Alarm is triggered when the duration of filter clogging exceeds the alarm time limit set in the system parameters. | Alarm |
| 86 | HPU +1MEX10 | Pressure filter - clogging tripg (-227H) | Alarm is triggered when the duration of filter clogging exceeds the trip time limit set in the system parameters. | Quick shutdown |
| 87 | HPU +1MEX10 | Return filter clogging warningg (-227I) | Alarm is triggered when the duration of filter clogging exceeds the alarm time limit set in the system parameters. | Alarm |
| 88 | HPU +1MEX10 | Return filter clogging tripg (-227I) | Alarm is triggered when the duration of filter clogging exceeds the trip time limit set in the system parameters. | Quick shutdown |
| 94 | HPU +1MEX10 | Accumulator pressure too high (-255E.2) | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Emergency shutdown |
| 384 | Common control and prot. +0CJA01 | Emergency shutdown button pressed (-S301) | Alarm is triggered when emergency shutdown pushbutton is pressed. | Emergency shutdown |
| 385 | Common control and prot. +0CJA01 | Emergency shutdown relay tripped (-K301) | Alarm is triggered when emergency shutdown is active. | Alarm |
| 389 | Common control and prot. +0CJA01 | Digital inputs power supply MCB (-F31) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 390 | Common control and prot. +0CJA01 | External signals power supply (-F36) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 392 | Common control and prot. +0CJA01 | Maintenance mode activated (-S100) | Alarm is triggered when when maintenance mode is active. | Emergency shutdown |
| 393 | Common control and prot. +0CJA01 | 24VDC MCBs group (-F37) - alarm | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Start interlock |
| 394 | Common control and prot. +0CJA01 | 24VDC MCBs group (-F34, -F38) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 396 | Common control and prot. +0CJA01 | Digital outputs power supply (-F32) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 410 | Common control +0CJA01 Comm. | Auxiliary meas. device Sentron PAC3220 - communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 411 | Common control +0CJA01 Comm. | 0BFA01 cubicle communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Emergency shutdown |
| 414 | Common control +0CJA01 Comm. | Unit 1 +1CJA01 Communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 415 | Common control +0CJA01 Comm. | Unit 2 +2CJA01 Communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 420 | Common control and prot. +0CJA01 | STI alarm from Intake +0LPY01 | Alarm is triggered when alarm is sent from another system via communication. | Start interlock |
| 421 | Common control and prot. +0CJA01 | NSD alarm from Intake +0LPY01 | Alarm is triggered when alarm is sent from another system via communication. | Normal shutdown |
| 422 | Common control and prot. +0CJA01 | QSD alarm from Intake +0LPY01 | Alarm is triggered when alarm is sent from another system via communication. | Quick shutdown |
| 423 | Common control and prot. +0CJA01 | ESD alarm from Intake +0LPY01 | Alarm is triggered when alarm is sent from another system via communication. | Emergency shutdown |
| 424 | Common control and prot. +0CJA01 | SICAM device power supply (-F39) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 425 | Common control and prot. +0CJA01 | 220VDC MCBs group (-F130) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 426 | Common control and prot. +0CJA01 | Aggregat 2 Emergency shutdown button pressed | Alarm is triggered when emergency shutdown pushbutton is pressed. | Emergency shutdown |
| 427 | HPU +1MEX10 | HPU Emergency shutdown button pressed | Alarm is triggered when emergency shutdown pushbutton is pressed. | Emergency shutdown |
| 428 | Common control and prot. +0CJA01 | Aggregat 1 Emergency shutdown button pressed | Alarm is triggered when emergency shutdown pushbutton is pressed. | Emergency shutdown |
| 440 | Common control and prot. +0CJA01 | Unit 1 stop from Remote station | Alarm is triggered when the command for shutdown of Unit 1 is received from the remote command centre. | Normal shutdown |
| 441 | Common control and prot. +0CJA01 | Unit 2 stop from Remote station | Alarm is triggered when the command for shutdown of Unit 2 is received from the remote command centre. | Normal shutdown |
| 442 | Common control and prot. +0CJA01 | Unit 1 block operation from Remote station | Alarm is triggered when the command for blocking start of Unit 1 is received from the remote command centre. | Normal shutdown |
| 443 | Common control and prot. +0CJA01 | Unit 2 block operation from Remote station | Alarm is triggered when the command for blocking start of Unit 2 is received from the remote command centre. | Normal shutdown |
| 448 | 220VDC Rectifier cubicle +0BDV01 | Rectifier failure (-KP1) | Alarm is triggered when the contact on the device is indicating that the fault has occured. | Emergency shutdown |
| 449 | 220VDC Rectifier cubicle +0BDV01 | AC input faliure (-KP2) | Alarm is triggered when the contact on the device is indicating that the fault has occured. | Emergency shutdown |
| 450 | 220VDC Rectifier cubicle +0BDV01 | DC output faliure (-KP3) | Alarm is triggered when the contact on the device is indicating that the fault has occured. | Emergency shutdown |
| 451 | 220VDC Rectifier cubicle +0BDV01 | Control supply fail (-FCP) | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 452 | 220VDC Rectifier cubicle +0BDV01 | Control voltage fail (-FDC) | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 453 | 220VDC Rectifier cubicle +0BDV01 | Main supply fail (-F0) | Alarm is triggered when CB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 454 | 220VDC Rectifier cubicle +0BDV01 | Service supply fail(-FS) | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 455 | 220VDC Rectifier cubicle +0BDV01 | Module suppy faul (-FM1, -FM2, - FM3) | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 456 | 220VDC Distrib. cubicle +0BVD02 | Main CB (-Q0) - ON | Alarm is triggered when CB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 457 | 220VDC Distrib. cubicle +0BVD02 | Unit 1 power supply (-F1) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 458 | 220VDC Distrib. cubicle +0BVD02 | Unit 2 power supply (-F2) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 459 | 220VDC Distrib. cubicle +0BVD02 | Common power supply 1 (-F3) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 460 | 220VDC Distrib. cubicle +0BVD02 | Common power supply 2 (-F4) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 461 | 220VDC Distrib. cubicle +0BVD02 | Unit 1 CWS valve motor MCB (-F5) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 462 | 220VDC Distrib. cubicle +0BVD02 | Unit 1 MV CB motor MCB (-F6) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 463 | 220VDC Distrib. cubicle +0BVD02 | Signal system supply 1 MCB (-F7) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 464 | 220VDC Distrib. cubicle +0BVD02 | Signal system supply 2 MCB (-F8) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 465 | 220VDC Distrib. cubicle +0BVD02 | Unit 1 DWS motor supply MCB (-F9) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 466 | 220VDC Distrib. cubicle +0BVD02 | Rectifier 1 24VDC MCB (-F10) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Normal shutdown |
| 467 | 220VDC Distrib. cubicle +0BVD02 | Rectifier 2 24VDC MCB (-F11) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Normal shutdown |
| 468 | 220VDC Distrib. cubicle +0BVD02 | Service voltage supply faiure (-FS) | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 482 | Auxiliary supply cubicle +0BFA01 | AC voltage not present (-F411, -K411) | Alarm is triggered when AC voltage is not present. | Emergency shutdown |
| 488 | Auxiliary supply cubicle +0BFA01 | Surge arrester (-FU1) - fault | Alarm is triggered when the surge arrestor is blown. | Normal shutdown |
| 493 | Auxiliary supply cubicle +0BFA01 | 24VDC MCBs group (-F31, -F422, -F39) - alarm | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Start interlock |
| 494 | Auxiliary supply cubicle +0BFA01 | 24VDC MCBs group (-F38) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Emergency shutdown |
| 500 | Auxiliary supply cubicle +0BFA01 | 24VDC Rectifier 1 (-F10, U101) - fault | Alarm is triggered when the rectifier is in state of fault. | Normal shutdown |
| 501 | Auxiliary supply cubicle +0BFA01 | 24VDC Rectifier 2 (-F11, U102) - fault | Alarm is triggered when the rectifier is in state of fault. | Normal shutdown |
| 503 | Auxiliary supply cubicle +0BFA01 | 24VDC Battery (-FB, -F40, -K201) - disconnected | Alarm is triggered when battery is disconnected. | Normal shutdown |
| 510 | Auxiliary supply cubicle +BFA01 | Common DC power supply MCB OFF (-F0) | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 511 | Auxiliary supply cubicle +0BFA01 | 220VDC Battery switch disconnector (-F0) - OFF | Alarm is triggered when the disconnector is OFF. | Normal shutdown |
| 512 | Auxiliary supply cubicle +0BFA01 | Incoming main supply CB (-Q0) - OFF | Alarm is triggered when CB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 521 | Common control and prot. +0CJA01 | Ventilation system not ready | Alarm is triggered when the ventilation system is indicating that it is not turned on. Acts as start blocking for Unit 2. | Normal shutdown |
| 523 | Auxiliary supply cubicle +0BFA01 | Unit 1 control cubicle +1CJA01 DC power suppply MCB (-F13) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 524 | Auxiliary supply cubicle +0BFA01 | Unit 2 control cubicle +2CJA01 DC power suppply MCB (-F14) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 526 | Auxiliary supply cubicle +0BFA01 | Unit 1 control cubicle +1CJA01 AC power suppply MCB (-F91) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 527 | Auxiliary supply cubicle +0BFA01 | Unit 2 control cubicle +2CJA01 AC power suppply MCB (-F92) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 529 | Auxiliary supply cubicle +0BFA01 | Common control cub. +0CJA01 AC power suppply MCB (-F93) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 534 | Auxiliary supply cubicle +0BFA01 | 220VDC rectifier cub. +0BDV01 AC power supply MCB (-F94) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 535 | Auxiliary supply cubicle +0BFA01 | Hatch house power supply MCB (-F67) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 536 | Auxiliary supply cubicle +0BFA01 | Variator power supply MCB (-F68) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 537 | Auxiliary supply cubicle +0BFA01 | Ventilation power supply MCB (-F69) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Normal shutdown |
| 540 | Auxiliary supply cubicle +0BFA01 | Metering cubicle +0CFA01 power supply MCB (-F62) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 541 | Auxiliary supply cubicle +0BFA01 | Powerhouse distribution panel power supply MCB (-F63) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 542 | Auxiliary supply cubicle +0BFA01 | External signals power supply (-F36) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 544 | Transformer feeder 1 +AKA01 | Disconnector (-Q1) - signalization error | Alarm is triggered when both the 'open' and 'closed' indications are either both inactive or both active. | Emergency shutdown |
| 545 | Transformer feeder 1 +AKA01 | Disconnector (-Q1) - OFF | Alarm is triggered when disconnector is OFF. | Emergency shutdown |
| 547 | Transformer feeder 1 +AKA01 | Earthing switch (-Q1) - signalization error | Alarm is triggered when both the 'open' and 'closed' indications are either both inactive or both active. | Emergency shutdown |
| 549 | Transformer feeder 1 +AKA01 | Earthing switch (-Q1) - grounded | Alarm is triggered when earthing switch is grounded. | Emergency shutdown |
| 579 | Transformer feeder 1 +AKA01 | Earthing switch (-Q1) - grounded | Alarm is triggered when earthing switch is grounded. | Emergency shutdown |
| 576 | Transformer feeder 2 +AKA02 | Disconnector (-Q2) - signalization error | Alarm is triggered when both the 'open' and 'closed' indications are either both inactive or both active. | Emergency shutdown |
| 577 | Transformer feeder 2 +AKA02 | Disconnector (-Q2) - OFF | Alarm is triggered when disconnector is OFF. | Emergency shutdown |
| 579 | Transformer feeder 2 +AKA02 | Earthing switch (-Q3) - signalization error | Alarm is triggered when both the 'open' and 'closed' indications are either both inactive or both active. | Emergency shutdown |
| 581 | Transformer feeder 2 +AKA02 | Earthing switch (-Q3) - grounded | Alarm is triggered when earthing switch is grounded. | Emergency shutdown |
| 656 | Common control and prot. +0CJA01 | Water measurement sensor - error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Alarm |
| 657 | Common control and prot. +0CJA01 | River water level measurement error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Alarm |
| 736 | Auxiliary supply cubicle +0BFA01 | Drainage pump 1 Minicass trip (-K100) | Alarm is triggered when the contact on the device is indicating that the fault has occured. | Quick shutdown |
| 737 | Auxiliary supply cubicle +0BFA01 | Drainage pump 1 Minicass MCB (-F32) OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 738 | Auxiliary supply cubicle +0BFA01 | Drainage pump 1 - control switch ON (-K102) | Alarm is triggered when the object is not in Auto control state. It functions as reminder that object might not function nominally in some conditions. | Alarm |
| 739 | Auxiliary supply cubicle +0BFA01 | Drainage pump 1 - control switch OFF(-K103) | Alarm is triggered when the object is not in Auto control state. It functions as reminder that object might not function nominally in some conditions. | Alarm |
| 740 | Auxiliary supply cubicle +0BFA01 | Drainage Pump 1 MCB (-K53) OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 741 | Auxiliary supply cubicle +0BFA01 | Drainage pump 2 Minicass trip (-K101) | Alarm is triggered when the contact on the device is indicating that the fault has occured. | Quick shutdown |
| 742 | Auxiliary supply cubicle +0BFA01 | Drainage pump 1 Minicass MCB (-F33) OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 743 | Auxiliary supply cubicle +0BFA01 | Drainage pump 2 - control switch ON (-K106) | Alarm is triggered when the object is not in Auto control state. It functions as reminder that object might not function nominally in some conditions. | Alarm |
| 744 | Auxiliary supply cubicle +0BFA01 | Drainage pump 2 - control switch OFF (-K107) | Alarm is triggered when the object is not in Auto control state. It functions as reminder that object might not function nominally in some conditions. | Alarm |
| 745 | Auxiliary supply cubicle +0BFA01 | Drainage Pump 2 MCB (-F54) OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Emergency shutdown |
| 746 | Auxiliary supply cubicle +0BFA01 | Drainage system water level too high | Alarm is triggered when the measurement surpasses a threshold set to be excessively high in the system parameters. | Quick shutdown |
| 757 | Auxiliary supply cubicle +0BFA01 | Pump 1 contactor - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |
| 760 | Auxiliary supply cubicle +0BFA01 | Pump 2 contactor - error | Alarm is triggered when the contactor activation command is activated, and the contactor does not carry out the requested operation within the time limit set in system parameters. Conversely, an alarm is also triggered when the contactor activation command is not activated, and the contactor is on. This could be due to intentional handling, wire break or a malfunction of the contactor or auxiliary contacts. | Alarm |

Intake alarm list and fault matrix

Table 4. Table of Intake alarms with IDs, descriptions, and classes.

| Alarm no. | Alarm system | Alarm name | Alarm description | Alarm type |
| --- | --- | --- | --- | --- |
| 105 | Intake cubicle +0LPY01 | Flap gate position measurement error | Alarm is triggered when the measurement signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Alarm |
| 106 | Intake cubicle +0LPY01 | Flap gate opening too long | Alarm is triggered when the gate open command is activated, and the gate fails to open within the time specified in the system parameters | Alarm |
| 107 | Intake cubicle +0LPY01 | Flap gate closing too long | Alarm is triggered when the gate close command is activated, and the gate fails to close within the time specified in the system parameters | Alarm |
| 110 | Intake cubicle +0LPY01 | Flap gate failure | Alarm is triggered when the gate indicates that it is in a state of failure. | Alarm |
| 259 | Intake cubicle +0LPY01 | UPS alarm | Alarm is triggered when the UPS system indicates that it is in alarm state. | Alarm |
| 260 | Intake cubicle +0LPY01 | UPS battery mode | Alarm is triggered when the UPS system indicates that it is working in battery mode. | Alarm |
| 261 | Intake cubicle +0LPY01 | UPS charging mode | Alarm is triggered when the UPS system indicates that it is working in charging mode. | Alarm |
| 294 | Intake cubicle +0LPY01 | Trash rack cleaner failure | Alarm is triggered when the Trash rack cleaner system indicates that it is in a failure state. | Alarm |
| 384 | Intake cubicle +0LPY01 | Emergency shutdown button pressed (-S301) | Alarm is triggered when emergency shutdown pushbutton is pressed. | Emergency shutdown |
| 385 | Intake cubicle +0LPY01 | Emergency shutdown relay tripped (-K301) | Alarm is triggered when emergency shutdown is active. | Alarm |
| 389 | Intake cubicle +0LPY02 | Digital inputs power supply - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 390 | Intake cubicle +0LPY01 | External signals power supply MCB (-F36) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 391 | Intake cubicle +0LPY01 | Analog inputs power supply MCB (-F33) - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 393 | Intake cubicle +0LPY01 | DC MCBs group (-F34) - alarm | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Alarm |
| 394 | Intake cubicle +0LPY01 | DC MCBs group (-F38) - trip | Alarm is triggered when at least one MCBs in the group is off. This could be due to intentional handling, wire breakage, or a malfunction of auxiliary contacts. | Alarm |
| 396 | Intake cubicle +0LPY02 | Digital outputs power supply - OFF | Alarm is triggered when MCB is off. This could be due to intentional handling, wire break or a malfunction of auxiliary contacts. | Alarm |
| 405 | Intake cubicle +0LPY01 | Common communication error | Alarm is triggered when a communication error occurs with the device. This can happen due to issues with cable termination or damage to the communication module on the device. | Alarm |
| 656 | Intake cubicle +0LPY01 | Water measurement sensor after trash rack - error | Alarm is triggered when the measurement signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Alarm |
| 657 | Intake cubicle +0LPY01 | Water measurement after trash rack - low | Alarm is triggered when the measurement falls below the low-value threshold set in the system parameters. | Start interlock |
| 658 | Intake cubicle +0LPY01 | Water measurement after trash rack - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters. | Normal shutdown |
| 659 | Intake cubicle +0LPY01 | Water measurement sensor before trash rack - error | Alarm is triggered when the current signal exceeds the nominal limits. Possible causes for this anomaly include issues such as improper cable termination at the measuring point, damage to the sensor or wire break. | Alarm |
| 660 | Intake cubicle +0LPY01 | Water measurement before trash rack - low | Alarm is triggered when the measurement falls below the low-value threshold set in the system parameters. | Start interlock |
| 661 | Intake cubicle +0LPY01 | Water measurement before trash rack - too low | Alarm is triggered when the measurement falls below a threshold that is set to be excessively low in the system parameters. | Normal shutdown |

# Unit 1 parameter list

Table 5. Table of Unit 1 parameters with IDs, descriptions, initial values, and units.

| Parameter no. | Parameter name | Parameter description | Initial value | Unit |
| --- | --- | --- | --- | --- |
| 1 | Generator active power nominal value | Specified value of a parameter under normal operating conditions. | 5330.0 | kW |
| 2 | Generator reactive power nominal value - high limit | Specified high limit value of a parameter under normal operating conditions. | 3802.0 | kVAr |
| 3 | Generator reactive power nominal value - low limit | Specified low limit value of a parameter under normal operating conditions. | -3802.0 | kVAr |
| 4 | Generator apparent power nominal value | Specified value of a parameter under normal operating conditions. | 6500.0 | kVA |
| 5 | Generator power factor nominal value - high limit | Specified high limit value of a parameter under normal operating conditions. | 0.82 | - |
| 6 | Generator power factor nominal value - low limit | Specified low limit value of a parameter under normal operating conditions. | 0.82 | - |
| 7 | Generator frequency nominal value | Specified value of a parameter under normal operating conditions. | 50.0 | Hz |
| 8 | Generator voltage nominal value | Specified value of a parameter under normal operating conditions. | 6600.0 | V |
| 9 | Generator current nominal value | Specified value of a parameter under normal operating conditions. | 569.0 | A |
| 10 | Grid voltage nominal value | Specified value of a parameter under normal operating conditions. | 6600.0 | V |
| 11 | Grid current nominal value | Specified value of a parameter under normal operating conditions. | 569.0 | A |
| 12 | Generator speed nominal value | Specified value of a parameter under normal operating conditions. | 300.0 | rpm |
| 14 | Low limit of measurement value is 0 | Low limit of measurement value is 0. | 0.0 | - |
| 16 | Turbine standstill time delay | Time that needs to pass from turbine stop to declare standstill. | T#15S | - |
| 17 | Turbine standstill MIV closed time delay | In case of speed sensor error, time that needs to pass from closing MIV to declare standstill of the turbine. | T#30M | - |
| 22 | Water level regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 0.1 | m |
| 23 | Water pressure regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 0.5 | bar |
| 24 | Active power regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 50.0 | kW |
| 25 | Position regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 1.0 | % |
| 28 | Number of water level measurements | Number that declares how many different water level measurements are present in the system. | 0 | - |
| 29 | Number of water pressure measurements | Number of water pressure measurements | 2 | - |
| 30 | Number of speed measurements | Number of speed measurements | 2 | - |
| 42 | Turbine pressure measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | bar |
| 43 | Turbine pressure measurement range high value | Parameter used to declare highest value of measurement range. | 5.0 | bar |
| 51 | Auto restart enabled | Function that starts shutdown of the Unit if the measurements that it is monitoring are approaching dangerously low/high values. After shutting down, monitoring of the measurements continues, and when measurements values get back to normal values, it initiates start of the Unit. | 0 | - |
| 52 | Minimal water level for auto restart | Value that declares minimal water level at which Auto Restart is initiated. | 0.2 | m |
| 55 | Local control switch exists | Parameter that declares if local control switch exists on control cubicle door. In case switch does not exist, local/remote control is set through HMI/SCADA. | 0 | - |
| 56 | Automatic control switch exists | Parameter that declares if automatic control switch exists on control cubicle door. In case switch does not exist, automatic/manual control is set through HMI/SCADA. | 0 | - |
| 59 | Generator minimal power | Minimal power at which GCB will switch off on shutdown | 100.0 | kW |
| 64 | Generator meas. device current meas scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 65 | Generator meas. device voltage meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 66 | Generator meas. device power meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 0.1 | - |
| 67 | Generator meas. device frequency meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 68 | Generator meas. device power factor meas. scaling fac. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 75 | Generator protection current meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 76 | Generator protection voltage meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 77 | Generator protection power meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 78 | Generator protection frequency meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 79 | Generator protection power factor meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 80 | Line protection current measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 81 | Line protection voltage measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 82 | Line protection power measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 83 | Line protection frequency measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 84 | Line protection power factor measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 85 | Line protection energy measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 86 | Excitation current measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 87 | Excitation voltage measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 88 | Excitation power measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 0.1 | - |
| 89 | Excitation frequency measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 90 | Excitation power factor measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 91 | Excitation field current scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1000.0 | - |
| 160 | Trafo temperature measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 161 | Trafo temperature measurement range high value | Parameter used to declare highest value of measurement range. | 120.0 | °C |
| 162 | Trafo temperature measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 163 | Trafo temperature measurement offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 164 | Trafo temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 85.0 | °C |
| 165 | Trafo temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 95.0 | °C |
| 166 | Export active energy factory unit | Parameter that declares unit of the energy counter. | 1.0 | MWh |
| 167 | Export reactive energy factory unit | Parameter that declares unit of the energy counter. | 0.0 | MVAr |
| 168 | Import active energy factory unit | Parameter that declares unit of the energy counter. | 0.0 | MWh |
| 228 | Minimal waterway pressure for MIV opening | Minimal pressure in waterway to allow the MIV to open. | 0.0 | bar |
| 229 | Maximal pressure differential for MIV opening | Maximal pressure difference between waterway and turbine to allow the MIV to open. | 3.0 | bar |
| 288 | Winding temperature measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 289 | Winding temperature measurement range high value | Parameter used to declare highest value of measurement range. | 150.0 | °C |
| 290 | Winding temperature scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 291 | Winding temperature scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 292 | Winding temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 100.0 | °C |
| 293 | Winding temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 110.0 | °C |
| 294 | Drive-endian temperature measurement range low value | Parameter used to declare lowest value of measurement range. | 1.0 | °C |
| 295 | Drive-endian temperature measurement range high value | Parameter used to declare highest value of measurement range. | 0.0 | °C |
| 296 | Drive-endian temperature scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 297 | Drive-endian temperature scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 298 | Drive-endian temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 73.0 | °C |
| 299 | Drive-endian temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 80.0 | °C |
| 300 | Not drive-endian temperature meas. range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 301 | Not drive-endian temperature meas. range high value | Parameter used to declare highest value of measurement range. | 120.0 | °C |
| 302 | Not drive-endian temperature scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 303 | Not drive-endian temperature scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 304 | Not drive-endian temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 70.0 | °C |
| 305 | Not drive-endian temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 77.0 | °C |
| 312 | Air outlet temperature measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 313 | Air outlet temperature measurement range high value | Parameter used to declare highest value of measurement range. | 150.0 | °C |
| 314 | Air outlet temperature scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 315 | Air outlet temperature scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | -15.0 | °C |
| 316 | Air outlet temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 60.0 | °C |
| 317 | Air outlet temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 70.0 | °C |
| 320 | Generator bearing temp. meas. range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 321 | Generator bearing temp. meas. range high value | Parameter used to declare highest value of measurement range. | 150.0 | °C |
| 322 | Generator bearing temp. meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 323 | Generator bearing temp. meas. offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 324 | Generator N bearing temp. high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 60.0 | °C |
| 325 | Generator N bearing temp. too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 67.0 | °C |
| 326 | Generator T bearing temp. high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 60.0 | °C |
| 327 | Generator T bearing temp. too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 67.0 | °C |
| 352 | Standstill speed relay | A value that indicates the speed limit below which it consideres that the turbine is in standstill. | 1.0 | % |
| 353 | Brake speed relay | A value that indicates the speed limit below which it considers that the turbine is braking. | 15.0 | % |
| 354 | Excitation speed relay | A value that indicates the speed limit above which it considers that the excication is ready to be turned on. | 95.0 | % |
| 355 | Synchronization speed relay | A value that indicates the speed limit above which it considers that the synchronization is ready to be performed. | 98.0 | % |
| 356 | Overspeed 1 speed relay | A value that indicates the speed limit above which it considers that the turbine speed is in overspeed 1. | 110.0 | % |
| 357 | Overspeed 2 speed relay | A value that indicates the speed limit above which it considers that the turbine speed is in overspeed 2. | 113.0 | % |
| 358 | Standstill hysteresis | A value that indicates speed limit above "standstill speed relay" value which it considers that the turbine is not longer in standstill. | 2.0 | % |
| 359 | Brake hysteresis | A value that indicates speed limit above "brake speed relay" value which it considers that the turbine is not longer braking. | 2.0 | % |
| 360 | Excitation hysteresis | A value that indicates speed limit below "excitation speed relay" value which it considers that the excitation is not longer ready to be turned on. | 5.0 | % |
| 361 | Synchronization hysteresis | A value that indicates speed limit below "synchronization speed relay" value which it considers that the synchronization is not ready to be performed. | 5.0 | % |
| 362 | Overspeed 1 hysteresis | A value that indicates speed limit below "overspeed 1 speed relay" value which it considers that the turbine is not longer in overspeed 1. | 5.0 | % |
| 363 | Overspeed 2 hysteresis | A value that indicates speed limit below "overspeed 2 speed relay" value which it considers that the turbine is not longer in overspeed 2. | 5.0 | % |
| 368 | Main speed measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | rpm |
| 369 | Main speed measurement range high value | Parameter used to declare highest value of measurement range. | 600.0 | rpm |
| 370 | Main speed scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 371 | Main speed scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | rpm |
| 372 | Redundant speed measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | rpm |
| 373 | Redundant speed measurement range high value | Parameter used to declare highest value of measurement range. | 600.0 | rpm |
| 374 | Redundant speed scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 375 | Redundant speed scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | rpm |
| 384 | Working hours DE bearing oil alarm | Value that indicates woking hours at which alarm is issued. | 3950.0 | h |
| 385 | Working hours DE bearing oil trip | Value that indicates woking hours at which trip is issued. | 4000.0 | h |
| 386 | Working hours NDE bearing oil alarm | Value that indicates woking hours at which alarm is issued. | 3950.0 | h |
| 387 | Working hours NDE bearing oil trip | Value that indicates woking hours at which trip is issued. | 4000.0 | h |
| 416 | Starting excitation regulation | 1 - Reactive power, 2 - Power factor, 3 - Voltage | 2 | - |
| 417 | Voltage regulation enabled | 0 - Voltage regulation disabled, 1 - Voltage regulation enabled | 0 | - |
| 418 | Convert PF or Q | 0 - No conversion, 1 - Convert Power factor to reactive power, 2 - Convert Reactive power to Power factor | 2 | - |
| 419 | Source of voltage matching | 0 - Synchronizator, 1 - PLC | 0 | - |
| 420 | Voltage OK | Minimal voltage percent of nominal generator voltage to check excitation function due to start command. | 0.8 | % |
| 421 | Excitation setpoint ramp time | Limit for slew rate of the output value in second in range absolute value. | 60.0 | s |
| 426 | Starting Q setpoint | Start Reactive power reference after synchronization. | 0.0 | kVar |
| 427 | Starting PF setpoint | Start Power factor reference after synchronization. | 1.0 | - |
| 428 | Starting U setpoint | Start Voltage reference after synchronization. | 6600.0 | V |
| 429 | Minimal Q setpoint | Minimal Reactive power reference on grid. | -3800.0 | kVar |
| 430 | Minimal PF setpoint | Minimal Power factor reference on grid. | 0.82 | - |
| 431 | Minimal U setpoint | Minimal Voltage reference on grid. | 6400.0 | V |
| 432 | Maximal Q setpoint | Maximal Reactive power reference on grid. | 3800.0 | kVar |
| 433 | Maximal PF setpoint | Maximal Power factor reference on grid. | 0.82 | - |
| 434 | Maximal U sepoint | Maximal Voltage reference on grid. | 6800.0 | V |
| 444 | Analog control fixed low limit | Low limit of the analog control for the excitation. | 0.0 | - |
| 445 | Analog control fixed high limit | High limit of the analog control for the excitation. | 27648.0 | - |
| 446 | Analog control fixed scaling factor | Scaling factor for the analog control for the excitation. | 1.0 | - |
| 447 | Analog control fixed offset | Offset for the analog control for the excitation. | 0.0 | - |
| 452 | Kaplan turbine distributor closed position value | Parameter used to declare "lowest" position value of kaplan turbine distributor. | 0.0 | % |
| 453 | Kaplan turbine distributor open position value | Parameter used to declare "highest" position value of kaplan turbine distributor. | 100.0 | % |
| 454 | Kaplan turbine distributor position offset | Constant value added to or subtracted from a measurement of kaplan distributor position to shift it to the desired reference point. | 0.0 | % |
| 455 | Kaplan turbine distributor position scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 456 | Kaplan turbine runner position value 1 | Parameter used to declare position 1 value of kaplan runner. | 100.0 | % |
| 457 | Kaplan turbine runner position value 2 | Parameter used to declare position 2 value of kaplan runner. | 0.0 | % |
| 458 | Kaplan turbine runner position offset | Constant value added to or subtracted from a measurement of kaplan runner position to shift it to the desired reference point. | 0.0 | % |
| 459 | Kaplan turbine runner position scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 512 | Number of valves in turbine | Number of valves in turbine. | 1 | - |
| 515 | Valve closed position | Value that declares the position in which valve is considered to be closed. Applies to all valves. | 0.5 | % |
| 516 | Valve open position | Value that declares the position in which valve is considered to be open. Applies to all valves | 99.5 | % |
| 519 | Speed up first point first valve position | Position of first valve in speed up. | 5.0 | - |
| 520 | Speed up first point second valve position | Position of second valve in speed up. | 0.0 | rpm |
| 521 | Speed up first point speed limit | Value that declares speed in which "speed up" transitions to the next point. | 25.0 | % |
| 522 | Speed up second point first valve position | Position of first valve in speed up. | 7.0 | % |
| 523 | Speed up second point second valve position | Position of second valve in speed up. | 0.0 | s |
| 524 | Speed up second point speed limit | Value that declares speed in which "speed up" transitions to the next point. | 50.0 | s |
| 525 | Speed up third point first valve position | Position of first valve in speed up. | 8.0 | s |
| 526 | Speed up third point second valve position | Position of second valve in speed up. | 0.0 | s |
| 527 | Speed up third point speed limit | Value that declares speed in which "speed up" transitions to the next point. | 75.0 | s |
| 528 | Sync follow grid frequency | 0 - Synchronizer giving up/down signals, 1 - Speed reference following grid frequency | 1 | s |
| 529 | Increment for speed reference | Value that declares the increment of speed reference due to synchronizer command. | 0.1 | s |
| 530 | Minimal power deflector reference | Value that declares the reference of the deflector valve at minimum power before switching on the regulation. | 18.0 | % |
| 531 | Minimal power synchronization nozzle reference | Value that declares the reference of the synchronization nozzle at minimum power before switching on the regulation. | 20.0 | % |
| 532 | Type of starting regulation on grid | 1 - Water level, 3 - Active power, 4 - Position | 4 | - |
| 533 | NSD first valve ramp time | Value that declares ramp time of first valve in case of normal shutdown. | 600.0 | s |
| 534 | QSD first valve ramp time | Value that declares ramp time of first valve in case of quick shutdown. | 0.0 | s |
| 535 | ESD first valve ramp time | Value that declares ramp time of first valve in case of emergency shutdown. | 0.0 | s |
| 536 | NSD second valve ramp time | Value that declares ramp time of second valve in case of normal shutdown. | 0.0 | s |
| 537 | QSD second valve ramp time | Value that declares ramp time of second valve in case of quick shutdown. | 0.0 | s |
| 538 | ESD second valve ramp time | Value that declares ramp time of second valve in case of emergency shutdown. | 0.0 | s |
| 541 | Auto alarms speed detection limit | A value that declares the speed below which a turbine fault is considered if this speed is not reached within the given time. | 5.0 | rpm |
| 542 | Auto alarms minimal valve position on grid | Value that declares minimal openness of valves while power plant is connected to the grid. | 15.0 | % |
| 543 | Auto alarms minimal water level | Value that declares minimal water level below which shutdown is activated. Power plant restarts automatically when water level rises above given limit. | -2.0 | m |
| 544 | Auto alarms maximal water level | Value that declares maximal water level at which Auto Restart is initiated. | 0.0 | m |
| 545 | Valve analog control value low | Low value for analog output for the control of the proportional valve of the Turbine. | -100.0 | - |
| 546 | Valve analog control value high | High value for analog output for the control of the proportional valve of the Turbine | 100.0 | - |
| 547 | Valve analog control offset | Offset for analog output for the control of the proportional valve of the Turbine. | 0.0 | - |
| 548 | Valve analog control scaling factor | Scaling factor for analog output for the control of the proportional valve of the Turbine. | 1.0 | - |
| 576 | Turbine bearing temp. meas. range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 577 | Turbine bearing temp. meas. range high value | Parameter used to declare highest value of measurement range. | 150.0 | °C |
| 578 | Turbine bearing temp. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 579 | Turbine bearing temp. scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | - |
| 580 | Turbine bearing temp. high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 40.0 | °C |
| 581 | Turbine bearing temp. too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 50.0 | °C |
| 582 | Turbine openness limiter value | Maximal openness of the turbine during limiter active | 80.0 | % |
| 583 | Turbine openness no limiter value | Maximal openness of the turbine during limiter not active | 90.0 | % |
| 584 | Timer for limiter exit | Time needed for limiter to stop working after conditions for no limit are met | T#10M | s |

Unit 2 parameter list

Table 6. Table of Unit 2 parameters with IDs, descriptions, initial values, and units.

| Parameter no. | Parameter name | Parameter description | Initial value | Unit |
| --- | --- | --- | --- | --- |
| 1 | Generator active power nominal value | Specified value of a parameter under normal operating conditions. | 672.0 | kW |
| 2 | Generator reactive power nominal value - high limit | Specified high limit value of a parameter under normal operating conditions. | 435.0 | kVAr |
| 3 | Generator reactive power nominal value - low limit | Specified low limit value of a parameter under normal operating conditions. | -435.0 | kVAr |
| 4 | Generator apparent power nominal value | Specified value of a parameter under normal operating conditions. | 800.0 | kVA |
| 5 | Generator power factor nominal value - high limit | Specified high limit value of a parameter under normal operating conditions. | 0.84 | - |
| 6 | Generator power factor nominal value - low limit | Specified low limit value of a parameter under normal operating conditions. | 0.84 | - |
| 7 | Generator frequency nominal value | Specified value of a parameter under normal operating conditions. | 50.0 | Hz |
| 8 | Generator voltage nominal value | Specified value of a parameter under normal operating conditions. | 380.0 | kV |
| 9 | Generator current nominal value | Specified value of a parameter under normal operating conditions. | 1291.0 | A |
| 10 | Grid voltage nominal value | Specified value of a parameter under normal operating conditions. | 380.0 | kV |
| 11 | Grid current nominal value | Specified value of a parameter under normal operating conditions. | 1291.0 | A |
| 12 | Generator speed nominal value | Specified value of a parameter under normal operating conditions. | 1000.0 | rpm |
| 14 | Low limit of measurement value is 0 | Low limit of measurement value is 0. | 0.0 | - |
| 16 | Turbine standstill time delay | Time that needs to pass from turbine stop to declare standstill. | T#15S | - |
| 17 | Turbine standstill MIV closed time delay | In case of speed sensor error, time that needs to pass from closing MIV to declare standstill of the turbine. | T#30M | - |
| 22 | Water level regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 0.1 | m |
| 23 | Water pressure regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 0.5 | bar |
| 24 | Active power regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 10.0 | kW |
| 25 | Position regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 1.0 | % |
| 28 | Number of water level measurements | Number that declares how many different water level measurements it is int the system. | 0 | - |
| 29 | Number of water pressure measurements | Number of water pressure measurements | 0 | - |
| 30 | Number of speed measurements | Number of speed measurements | 1 | - |
| 51 | Auto restart enabled | Function that starts shutdown of the Unit if the measurements that it is monitoring are approaching dangerously low/high values. After shutting down, monitoring of the measurements continues, and when measurements values get back to normal values, it initiates start of the Unit. | 0 | - |
| 52 | Minimal water level for auto restart | Value that declares minimal water level at which Auto Restart is initiated. | 0.2 | m |
| 55 | Local control switch exists | Parameter that declares if local control switch exists on control cubicle door. In case switch does not exist, local/remote control is set through HMI/SCADA. | 0 | - |
| 56 | Automatic control switch exists | Parameter that declares if automatic control switch exists on control cubicle door. In case switch does not exist, automatic/manual control is set through HMI/SCADA. | 0 | - |
| 59 | Generator minimal power | Minimal power at which GCB will switch off on shutdown | 60.0 | kW |
| 75 | Generator protection current meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | m |
| 76 | Generator protection voltage meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 77 | Generator protection power meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 78 | Generator protection frequency meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 79 | Generator protection power factor meas. scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 85 | Line protection energy measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 166 | Export active energy factory unit | Parameter that declares unit of the energy counter. | 1.0 | MWh |
| 167 | Export reactive energy factory unit | Parameter that declares unit of the energy counter. | 0.0 | Mvarh |
| 168 | Import active energy factory unit | Parameter that declares unit of the energy counter. | 0.0 | MWh |
| 228 | Minimal waterway pressure for MIV opening | Minimal pressure in waterway to allow the MIV to open. | 0.0 | bar |
| 229 | Maximal pressure differential for MIV opening | Maximal pressure difference between waterway and turbine to allow the MIV to open. | 1.5 | bar |
| 288 | Winding temperature measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 289 | Winding temperature measurement range high value | Parameter used to declare highest value of measurement range. | 150.0 | °C |
| 290 | Winding temperature scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 291 | Winding temperature scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 292 | Winding temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 125.0 | °C |
| 293 | Winding temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 140.0 | °C |
| 294 | Drive-endian temperature measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 295 | Drive-endian temperature measurement range high value | Parameter used to declare highest value of measurement range. | 120.0 | °C |
| 296 | Drive-endian temperature scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 297 | Drive-endian temperature scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 298 | Drive-endian temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 85.0 | °C |
| 299 | Drive-endian temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 95.0 | °C |
| 300 | Not drive-endian temperature meas. range low value | Parameter used to declare lowest value of measurement range. | 0.0 | °C |
| 301 | Not drive-endian temperature meas. range high value | Parameter used to declare highest value of measurement range. | 120.0 | °C |
| 302 | Not drive-endian temperature scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 303 | Not drive-endian temperature scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | °C |
| 304 | Not drive-endian temperature high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 85.0 | °C |
| 305 | Not drive-endian temperature too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 95.0 | °C |
| 318 | Thrust temperature high | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 65.0 | °C |
| 319 | Thrust temperature too high | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 72.0 | °C |
| 352 | Standstill speed relay | A value that indicates the speed limit below which it consideres that the turbine is in standstill. | 25.0 | % |
| 353 | Brake speed relay | A value that indicates the speed limit below which it considers that the turbine is braking. | 15.0 | % |
| 354 | Excitation speed relay | A value that indicates the speed limit above which it considers that the excication is ready to be turned on. | 95.0 | % |
| 355 | Synchronization speed relay | A value that indicates the speed limit above which it considers that the synchronization is ready to be performed. | 98.0 | % |
| 356 | Overspeed 1 speed relay | A value that indicates the speed limit above which it considers that the turbine speed is in overspeed 1. | 110.0 | % |
| 357 | Overspeed 2 speed relay | A value that indicates the speed limit above which it considers that the turbine speed is in overspeed 2. | 120.0 | % |
| 358 | Standstill hysteresis | A value that indicates speed limit above "standstill speed relay" value which it considers that the turbine is not longer in standstill. | 2.0 | % |
| 359 | Brake hysteresis | A value that indicates speed limit above "brake speed relay" value which it considers that the turbine is not longer braking. | 2.0 | % |
| 360 | Excitation hysteresis | A value that indicates speed limit below "excitation speed relay" value which it considers that the excitation is not longer ready to be turned on. | 5.0 | % |
| 361 | Synchronization hysteresis | A value that indicates speed limit below "synchronization speed relay" value which it considers that the synchronization is not ready to be performed. | 5.0 | % |
| 362 | Overspeed 1 hysteresis | A value that indicates speed limit below "overspeed 1 speed relay" value which it considers that the turbine is not longer in overspeed 1. | 5.0 | % |
| 363 | Overspeed 2 hysteresis | A value that indicates speed limit below "overspeed 2 speed relay" value which it considers that the turbine is not longer in overspeed 2. | 5.0 | % |
| 368 | Main speed measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | rpm |
| 369 | Main speed measurement range high value | Parameter used to declare highest value of measurement range. | 1500.0 | rpm |
| 370 | Main speed scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 0.3333334 | - |
| 371 | Main speed scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | rpm |
| 384 | Working hours DE bearing oil alarm | Value that indicates woking hours at which alarm is issued. | 3950.0 | h |
| 385 | Working hours DE bearing oil trip | Value that indicates woking hours at which trip is issued. | 4000.0 | h |
| 386 | Working hours NDE bearing oil alarm | Value that indicates woking hours at which alarm is issued. | 3950.0 | h |
| 387 | Working hours NDE bearing oil trip | Value that indicates woking hours at which trip is issued. | 4000.0 | h |
| 448 | Francis turbine distributor closed position value | Parameter used to declare "lowest" position value of francis turbine distributor. | 0.0 | % |
| 449 | Francis turbine distributor open position value | Parameter used to declare "highest" position value of francis turbine distributor. | 100.0 | % |
| 450 | Francis turbine distributor position offset | Constant value added to or subtracted from a measurement of francis distributor position to shift it to the desired reference point. | 0.0 | % |
| 451 | Francis turbine distributor position scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 512 | Number of valves in turbine | Number of valves in turbine. | 1 | - |
| 515 | Valve closed position | Value that declares the position in which valve is considered to be closed. Applies to all valves. | 0.5 | % |
| 516 | Valve open position | Value that declares the position in which valve is considered to be open. Applies to all valves | 99.5 | % |
| 519 | Speed up first point first valve position | Position of first valve in speed up. | 2.0 | % |
| 520 | Speed up first point second valve position | Position of second valve in speed up. | 0.0 | % |
| 521 | Speed up first point speed limit. | Value that declares speed in which “speed up” transitions to the next point. | 25.0 | % |
| 522 | Speed up second point first valve position | Position of first valve in speed up. | 3.0 | % |
| 523 | Speed up second point second valve position | Position of second valve in speed up. | 0.0 | % |
| 524 | Speed up second point speed limit | Value that declares speed in which “speed up” transitions to the next point. | 50.0 | % |
| 525 | Speed up third point first valve position | Position of first valve in speed up. | 4.0 | % |
| 526 | Speed up third point second valve position | Position of second valve in speed up. | 0.0 | % |
| 527 | Speed up third point speed limit | Value that declares speed in which “speed up” transitions to the next point. | 75.0 | % |
| 528 | Sync follow grid frequency | 0 - Synchronizer giving up/down signals, 1 - Speed reference following grid frequency | 1 | s |
| 529 | Increment for speed reference | Value that declares the increment of speed reference due to synchronizer command. | 0.1 | rpm |
| 530 | Minimal power deflector reference | Value that declares the reference of the deflector valve at minimum power before switching on the regulation. | 18.0 | % |
| 531 | Minimal power synchronization nozzle reference | Value that declares the reference of the synchronization nozzle at minimum power before switching on the regulation. | 20.0 | s |
| 532 | Type of starting regulation on grid | 1 - Water level, 3 - Active power, 4 - Position | 4 | s |
| 533 | NSD first valve ramp time | Value that declares ramp time of first valve in case of normal shutdown. | 120.0 | s |
| 534 | QSD first valve ramp time | Value that declares ramp time of first valve in case of quick shutdown. | 60.0 | s |
| 535 | ESD first valve ramp time | Value that declares ramp time of first valve in case of emergency shutdown. | 0.0 | s |
| 536 | NSD second valve ramp time | Value that declares ramp time of second valve in case of normal shutdown. | 180.0 | s |
| 537 | QSD second valve ramp time | Value that declares ramp time of second valve in case of quick shutdown. | 60.0 | s |
| 538 | ESD second valve ramp time | Value that declares ramp time of second valve in case of emergency shutdown. | 0.0 | s |
| 541 | Auto alarms speed detection limit | A value that declares the speed below which a turbine fault is considered if this speed is not reached within the given time. | 5.0 | % |
| 542 | Auto alarms minimal valve position on grid | Value that declares minimal openness of valves while power plant is connected to the grid. | 15.0 | % |
| 543 | Auto alarms minimal water level | Value that declares minimal water level below which shutdown is activated. Power plant restarts automatically when water level rises above given limit. | -2.0 | m |
| 544 | Auto alarms maximal water level | Value that declares maximal water level at which Auto Restart is initiated. | 0.0 | m |
| 582 | Turbine openness limiter value | Maximal openness of the turbine during limiter active | 80.0 | % |
| 583 | Turbine openness no limiter value | Maximal openness of the turbine during limiter not active | 90.0 | % |
| 584 | Timer for limiter exit | Time needed for limiter to stop working after conditions for no limit are met | T#10M | s |

Common parameter list

Table 7.Table of Common parameters with IDs, descriptions, initial values, and units.

| Parameter no. | Parameter name | Parameter description | Initial value | Unit |
| --- | --- | --- | --- | --- |
| 1 | HPP active power nominal value | Specified value of a parameter under normal operating conditions. | 6200.0 | kW |
| 2 | HPP reactive power nominal value - high limit | Specified high limit value of a parameter under normal operating conditions. | 3500.0 | kVAr |
| 3 | HPP reactive power nominal value - low limit | Specified low limit value of a parameter under normal operating conditions. | -3500.0 | kVAr |
| 4 | HPP apparent power nominal value | Specified value of a parameter under normal operating conditions. | 7000.0 | kVA |
| 5 | HPP power factor nominal value - high limit | Specified high limit value of a parameter under normal operating conditions. | 0.82 | - |
| 6 | HPP power factor nominal value - low limit | Specified low limit value of a parameter under normal operating conditions. | 0.82 | - |
| 7 | HPP frequency nominal value | Specified value of a parameter under normal operating conditions. | 50.0 | Hz |
| 8 | HPP voltage nominal value | Specified value of a parameter under normal operating conditions. | 12.0 | kV |
| 9 | HPP current nominal value | Specified value of a parameter under normal operating conditions. | 50.0 | A |
| 10 | Grid voltage nominal value | Specified value of a parameter under normal operating conditions. | 12.0 | kV |
| 11 | Grid current nominal value | Specified value of a parameter under normal operating conditions. | 50.0 | A |
| 12 | Generator speed nominal value | Specified value of a parameter under normal operating conditions. | 750.0 | rpm |
| 14 | Low limit of measurement value is 0 | Low limit of measurement value is 0. | 0.0 | - |
| 22 | Water level regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 0.1 | m |
| 24 | Active power regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 10.0 | kW |
| 28 | Number of water level measurements | Defines number of available Water level measurements. | 1 | - |
| 40 | Intake water level too low value | Value indicating the limit below which the measurement value is not in allowed range. Triggers an alarm. | -2.3 | m |
| 41 | Intake water level low value | Value indicating the limit below which the measurement value is at the lower end of allowed range. Triggers an alarm. | -2.12 | m |
| 55 | Local control switch exists | Parameter that declares if local control switch exists on control cubicle door. In case switch does not exist, local/remote control is set through HMI/SCADA. | 0 | - |
| 56 | Automatic control switch exists | Parameter that declares if automatic control switch exists on control cubicle door. In case switch does not exist, automatic/manual control is set through HMI/SCADA. | 0 | - |
| 57 | Power scheduling locking hour | Parameter that declares hour in the day when tomorrow table for power scheduling is locked for editing. Editing can still be done using administrator credentials. | 18 | h |
| 59 | Unit 1 Nominal Power | Parameter that specifies the nominal power of the unit. Used to limit the output of common power regulation based on the number of units in remote common regulation. | 5700.0 | kW |
| 60 | Unit 2 Nominal Power | Parameter that specifies the nominal power of the unit. Used to limit the output of common power regulation based on the number of units in remote common regulation. | 690.0 | kW |
| 61 | Unit 3 Nominal Power | Parameter that specifies the nominal power of the unit. Used to limit the output of common power regulation based on the number of units in remote common regulation. | 0.0 | kW |
| 69 | Auxiliary meas. device current meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 70 | Auxiliary meas. device voltage meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 71 | Auxiliary meas. device power meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 72 | Auxiliary meas. device frequency meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 73 | Auxiliary meas. device power factor meas. scaling fact. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 74 | Auxiliary meas. device energy meas. scaling factor. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 0.1 | - |
| 85 | Line protection energy measurement scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 142 | Intake water level measurement range low value | Parameter used to declare lowest value of measurement range. | 236.8 | m |
| 143 | Intake water level measurement range high value | Parameter used to declare highest value of measurement range. | 241.8 | m |
| 144 | Intake water level scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 145 | Intake water level offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | m |
| 146 | River water level measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | m |
| 147 | River water level measurement range high value | Parameter used to declare highest value of measurement range. | 4.0 | m |
| 148 | River water level scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 149 | River water level scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.43 | m |
| 150 | Tail water level measurement range low value | Parameter used to declare lowest value of measurement range. | 0.0 | m |
| 151 | Tail water level measurement range high value | Parameter used to declare highest value of measurement range. | 4.0 | m |
| 152 | Tail water level scaling factor | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 153 | Tail water level scaling offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 48.23 | m |
| 154 | Tail water level high value | Value indicating the limit above which the measurement value is at the higher end of allowed range. Triggers an alarm. | 50.0 | m |
| 155 | Tail water level too high value | Value indicating the limit above which the measurement value is not in allowed range. Triggers an alarm. | 60.0 | m |
| 166 | Export active energy unit | Defines unit of the energy counter. | 1.0 | MWh |
| 167 | Export reactive energy unit | Defines unit of the energy counter. | 0.0 | MVArh |
| 168 | Import active energy unit | Defines unit of the energy counter. | 0.0 | MWh |
| 192 | Start regulation on grid | Defines start regulation on the grid: 0 - Water level regulation, 1 - Active power regulation | 0 | - |
| 194 | Start number of units | 0 - Start unit with the first priority, 1 - start all units | 0 | - |
| 195 | Unit ramp up time | Defines up ramp time for Unit openness after synchronization until switch to regulation mode. Active only in switch from one to two units operation. Purpose of up ramp time is that power plant keeps stable Active power value until the Unit that is starting switches to regulation mode. | 600.0 | s |
| 196 | Unit ramp down time | Defines down ramp time for Unit openness after swtich from regulation mode to start of shutdown sequence. Active only in switch from two to one unit operation. Purpose of down ramp time is that power plant keeps stable Active power value until the Unit that is stopping initiates stopping sequence. | 3600.0 | s |
| 197 | Start unit value | Defines openness setpoint from Common control Active power regulator above which value Common control sends request to the Unit with lower level of priority to start. | 98.0 | % |
| 198 | Stop unit value | Defines openness setpoint from Common control Active power regulator below which value Common control sends request to the Unit with lowest priority to stop. | 35.0 | % |
| 199 | Start unit delay | Defines time delay that is active from the moment when Common control sends start request to Unit. When defined time delay passes, Unit initiates starting sequence. Purpose of Start Unit delay timer is to eliminate unnecessary starting of the Unit if the conditions for starting the unit are transient. | T#10M | s |
| 200 | Stop unit delay | Defines time delay that is active from the moment when Common control sends stop request to Unit. When defined time delay passes, Unit initiates stopping sequence. Purpose of Stop Unit delay timer is to eliminate unnecessary stopping of the Unit if the conditions for stopping the unit are transient. | T#10M | s |
| 224 | HPU pump regulation high limit value | Upper (high) limit for regulation. | 50.0 | bar |
| 225 | HPU pump regulation area value | Area (from upper limit to lower limit) of regulation. | 10.0 | bar |

Intake parameter list

Table 8. Table of Intake parameters with IDs, descriptions, initial values, and units.

| Parameter no. | Parameter name | Parameter description | Initial value | Unit |
| --- | --- | --- | --- | --- |
| 1 | Flap gate position measurement - value low | Parameter used to declare lowest value of measurement range. | 0.0 | % |
| 2 | Flap gate position measurement - value high | Parameter used to declare highest value of measurement range. | 100.0 | % |
| 3 | Flap gate position measurement - scal. Fac | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 4 | Flap gate position measurement - offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | - |
| 64 | Water level after trash rack - value low | Parameter used to declare lowest value of measurement range. | 0.0 | m |
| 65 | Water level after trash rack - value high | Parameter used to declare highest value of measurement range. | 20.0 | m |
| 66 | Water level after trash rack - scal. Fac. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 67 | Water level after trash rack - offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 69.69 | - |
| 68 | Water level before trash rack - value low | Parameter used to declare lowest value of measurement range. | 0.0 | m |
| 69 | Water level before trash rack - value high | Parameter used to declare highest value of measurement range. | 5.0 | m |
| 70 | Water level before trash rack - scal. Fac. | Constant multiplier used to relate the value or reading obtained from a measurement instrument to the actual physical quantity being measured. | 1.0 | - |
| 71 | Water level before trash rack - offset | Constant value added to or subtracted from a measurement or reading to shift it to the desired reference point or baseline. | 0.0 | - |
| 192 | Flap gate open limit | Defines number that represents open position for Flap gate | 99.5 | % |
| 193 | Flap gate close limit | Defines number that represents closed position for Flap gate | 0.5 | % |
| 224 | Cleaner working mode | 0 - Cyclic , 1 - Water level difference, 2- Cleaner scheduling | 0 | - |
| 225 | Cleaner start interval | This parameter defines how often the system sends an automatic start command to the cleaner. | T#11H_59M | s |
| 226 | Water level difference for cleaner start | This parameter sets the minimum water level difference between the level before and after trash rack required to trigger the cleaner. If the difference exceeds the defined threshold, a cleaning cycle is initiated. | 0.5 | m |
| 288 | Local/remote control switch exists | Parameter used to define if local/remote switch exists on the cubicle. If the parameter is set to 0 - system uses SCADA button to change local/remote mode, if the parameter is set to 1 - system uses physical swtich on the cubicle to change local/remote mode. | 0 | - |
| 289 | Auto/man control sw exists | Parameter used to define if auto/manual switch exists on the cubicle. If the parameter is set to 0 - system uses SCADA button to change auto/manual mode, if the parameter is set to 1 - system uses physical swtich on the cubicle to change auto/manual mode. | 0 | - |
| 290 | Water level regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 1.0 | m |
| 291 | Flap gate position regulation increment | Adjustment value added to the setpoint of regulation by clicking increment/decrement buttons on SCADA/HMI. | 5.0 | % |
| 294 | Number of water level measurements | Defines number of available Water level measurements. | 1 | - |
| 295 | Water level regulation winter reference | This parameter defines the target water level used for regulation during winter operation. | 70.99 | m |
| 296 | Water level regulation summer reference | This parameter defines the target water level used for regulation during summer operation. | 70.99 | m |
| 297 | Water level reference intake offset | Constant value added to powerplant water level regulation reference for regulation of water level on intake. It makes difference between powerplant and intake water level regulators references required for proper functionality of the system. | 0.1 | m |
| 298 | Water level maximum reference | Value that declares maximum allowed reference for water level regulation on intake. | 71.5 | m |
| 299 | Water level minimum reference | Value that declares minimum allowed reference for water level regulation on intake. | 70.5 | m |
| 320 | Water level after trash rack - low | Value indicating the limit below which the measurement value is at the lower end of allowed range. Triggers an alarm. | 70.55 | m |
| 321 | Water level after trash rack - too low | Value indicating the limit below which the measurement value is not in allowed range. Triggers an alarm. | 70.5 | m |
| 322 | Water level before trash rack - low | Value indicating the limit below which the measurement value is at the lower end of allowed range. Triggers an alarm. | 120.0 | m |
| 323 | Water level before trash rack - too low | Value indicating the limit below which the measurement value is not in allowed range. Triggers an alarm. | 1.0 | m |